Texas Nodal

Energy Management System

Software Requirements Specification

For Wind Power Forecasting

Version 1.0

Revision History

| Date | Version | Description | Author |
| --- | --- | --- | --- |
| 12/01/2006 | 0.90 | These requirements were developed through an iterative process and reviewed by various ERCOT teams, including Nodal EMS team, Nodal IDA team, ERCOT Operations and IT Support teams, as well as EMS vendor. | Nodal EMS Team |
| 2/16/2007 | 0.91 | Updated for TPTF Comments | Nodal EMS Team |
| 3/09/2007 | 1.0 | TPTF Approved; Compliant with February 2007 Nodal Protocols; Actual Protocol reference number convention is from the May 2006 Nodal Protocols, except where noted. | Nodal EMS Team |

Table of Contents

1.	Introduction	6

1.1	Purpose	6

1.2	Objectives	6

1.3	Scope	6

1.4	Traceability	7

2.	Wind Power Production Potential	8

2.1	WPF Inputs and Outputs	9

2.2	WPF Functional Diagrams	10

2.3	Preconditions and Dependencies	12

3.	Functional Requirements	13

3.1	Short Term Wind Production Forecast	13

3.2	WGRPP Forecast	13

3.3	LTWPF Profiles	13

3.4	WPF Data Posting	14

3.5	Actual Wind Generation and Meteorological Data Archive	14

3.6	WPF Forecasts Archive	14

4.	Supplementary Requirements	16

4.1	Availability Requirements	16

4.2	Performance Requirements	16

4.3	Forecast Accuracy Requirements	16

4.4	STWPF Self-Training	17

4.5	Data Validation	17

4.6	Usability	18

4.7	Security	18

5.	Protocol Coverage	19

This page is intentionally left blank.

Software Requirements Specification

This Requirements Document is Subordinate To and Compliant with the Texas Nodal Protocols Effective February 2007.

# Introduction

The requirements for Texas Nodal market implementation are described in the Texas Nodal Protocols.  This document focuses on elaborating the requirements for the Wind Power Forecasting (WPF) process of the Energy Management System.

This Requirements Specification is a part of the complete set of specification documents for the Texas Nodal market implementation.  For implementation purposes the Texas Nodal market functions are categorized into multiple systems based on clear distinction in functionality.  The WPF is one of these systems.

The WPF requirements are documented in the Texas Nodal EMS Requirements Specification document; supplemented by the following Requirements Specifications:

- Texas Nodal EMS Data Model Requirements Specification

- Texas Nodal EMS SCADA Requirements Specification

- Texas Nodal EMS Dynamic Ratings Requirements Specification

- Texas Nodal EMS Forced Outage Detection Requirements Specification

- Texas Nodal EMS Generation Sub-system Requirements Specification

- Texas Nodal EMS Load Forecasting Requirements Specification

- Texas Nodal EMS Wind Power Forecasting Requirements Specification

- Texas Nodal EMS State Estimator Requirements Specification

- Texas Nodal EMS Network Security and Stability Analysis Requirements Specification

- Texas Nodal EMS Voltage Support Requirements Specification

- Texas Nodal EMS Outage Evaluation Requirements Specification

The definitions and acronyms from Section 2 of the Protocols are used in this document as applicable.

## Purpose

The primary purpose of this requirements specification document is to fully describe the external behavior of the WPF process.  It also describes nonfunctional requirements, design constraints, and other factors necessary to provide a complete and comprehensive description of the requirements necessary to design and develop the corresponding software systems.

## Objectives

The objectives of this requirements specification are to:

- Specify mutually exclusive and collectively exhaustive set of requirements for the WPF process

- Ensure that requirements are in compliance with the Nodal Protocols

- Ensure that requirements are traceable to Nodal Protocols, NERC, FERC and any other applicable standards

## Scope

The scope of this document is to elicit requirements for the WPF process to be in compliance with the Nodal Protocols published in May 2006, NERC, FERC and PUCT guidelines.  However, elaborating requirements that would change the intent of the protocols or proposing a design for the system is outside the scope of this document.  To ensure compliance the designers and developers of the systems are required to read and understand the Nodal Protocols.

Any scope changes to this requirements specification due to alternate design proposals must be driven by Nodal Protocol Revision Request (NPRR) and channeled through Nodal Change Control Board (CCB).  Any scope changes to this requirements specification due to further elaboration, while still being in compliance with Nodal Protocols, must be channeled through Nodal CCB.

## Traceability

All WPF functional requirements are traceable to at least one of the following governing documents: Nodal Protocols, NERC standards, FERC guidelines, and PUCT documents.  In addition requirements are traceable to the Process Map that describes the WPF process.

# Wind Power Production Potential

The WPF process is a new ERCOT process that utilizes a combination of ERCOT systems and an external system (wind power production forecasting service) to produce the Short-Term Wind Power Forecasts (STWPF) and derive the Wind-Powered Generation Resource Production Potential (WGRPP).  The Long-Term Wind Power Forecasts (LTWPF) are provided by Wind-Powered Generation Resources (WGR) to ERCOT.

The STWPF is a forecast for the next 48 hours by hour of the “expected” wind power produced by each wind facility (farm).  This forecast is equivalent to the center of the expected power output probability distribution, hour by hour, for the next 48 hours.

Similarly, the WGRPP is a forecast for the next 48 hours of potential wind power output.  Unlike the STWPF however, the WGRPP is not the “expected” wind power, but the facility power output with an 80% confidence level the facility will exceed.

The LTWPF, is similar to the STWPF in that it is a forecast of “expected” power production.  Unlike the STWPF, the LTWPF is provided by the facility operator, and is a “typical” energy profile for each day of a future month.  Thus, ERCOT will have an “expected” wind profile for any day of the next year provided by the facility owner, and will have the STWPF for the next 48 hours.   ERCOT expects WGR Entities to analyze historic wind speeds for each month to provide a statistical “normal” daily profile for each month, but the methodology used for the LTWPF is outside the scope of this document.

The WPF process is compromised of several sub-processes: asset registration, real-time data collection, review of wind farm availability schedules, forecasting, and providing the resulting forecasts to the required recipients.

Asset registration is an existing ERCOT business process.  The WPF process requires additional registration data from new and existing WGRs.  The updated generation asset registration form allows collection of the required additional specification data.  Existing WGRs shall update their registration information to ensure all wind generators have provided all required information. Required specification data are listed below in Table 1.

Operational (real-time) data from all generator types is provided by QSE’s through telemetry to the ERCOT Energy Management System (EMS).  The WPF process will require additional operational data from wind generators through telemetry.  Required operational data are listed below in Table 1.

The WPF process checks for the availability of the wind farms as scheduled by QSEs in the Outage Scheduler.

All the aforementioned data inputs (specification data, operational data and unit availability) are provided by ERCOT to the wind power production forecasting service for utilization along with their additional meteorological information to calculate the STWPF and the WGRPP.  These forecasts are shared with the market as appropriate.  A QSE representing a WGR must enter a High Sustainable Limit (HSL) value in their Current Operating Plan that is less than or equal to the amount for that wind farm from the most recent WGRPP provided by ERCOT.  The HSL values in the Current Operating Plan provided by QSE’s are inputs to the Reliability Unit Commitment processes.  All forecasts are made available for use by ERCOT for operating and planning purposes.

## WPF Inputs and Outputs

This section provides a summary of inputs and outputs to the Wind Power Forecasting process. Table 1 lists all the required input data from ERCOT to the WPF process. The “Source” column of the input table identifies where the data is provided to the WPF process.

Table 1 : WPF Process Inputs

| Source | Data |
| --- | --- |
| Registration system | - Resource Parameters - Resource Name - Location of wind farm (latitude and longitude or equivalent for the center point of wind farm) - Location of the meteorological tower (latitude and longitude or equivalent) - Type (manufacturer/model) and number of turbines - Turbine hub height(s) above ground level with associated number of turbines - Manufacturer’s power curve (capability curve) - Resource-QSE mapping - Resource Commercial Operation Date |
| Outage Scheduler | Scheduled outages of wind farms |
| Energy Management System (EMS) | - Most recent Resource (wind farm) status with date/time - Most recent MW output of wind farm with date/time - Most recent wind speed and direction at hub height from one meteorological tower with date/time - Temperature and barometric pressure at 2 m above ground level on the meteorological tower |
| Vendor | Regional Weather Data |

Table 2 lists outputs from the WPF process to various systems. The “Destination” column of the output table identifies the target for the data generated by the WPF process.  Note that the Market Information System (MIS) manages market participant specific data and public data. Some data is required to be provided through the Messaging System to QSE’s.

Table 2 : WPF Process Outputs

| Destination | Data |
| --- | --- |
| Market Information System (MIS) | - Aggregated STWPF for ERCOT – (Secured Area) - STWPF for each WGR (Certified Area) - WGRPP for ERCOT – (Secured Area) - WGRPP for each WGR (Certified Area) |
| Data Archive (EDW) | - Aggregated STWPF for ERCOT - Aggregated WGRPP for ERCOT - LTWPF for each WGR - System performance metrics from requirement SR4 and SR5 - Actual wind speed, temperature, barometric pressure, and power output from each WGR - Each STWPF forecast and associated wind speeds with date/time forecasted, and date/time of forecast for each WGR. - Each WGRPP forecast and associated wind speeds with date/time forecasted, and date/time of forecast and probability distribution table for each WGR - Each LTWPF received with associated WGR, date/time of receipt, applicable month/year, and hourly wind forecast. |

## WPF Functional Diagrams

Figure 1 below depicts the inputs and outputs of the Wind Power Production Forecasting service with respect to the STWPF and the WGRPP. The LTWPF information is sent by WGRs to ERCOT.

Figure 1 Brief description:  Wind Generating Resources shall provide specification data of wind farms to ERCOT during the registration process.  Qualified Scheduling Entities representing Wind Generating Resources shall provide to ERCOT the unit availability information through the Current Operating Plan, Outage Scheduler and operational data from wind farms into the Energy Management System.  ERCOT sends the operational data and the specification data to the wind power production forecasting service.  The STWPF and WGRPP forecasts are calculated by the wind power production forecasting service and sent to ERCOT, who makes the forecasts available to the MIS for use by the QSE to update the Current Operating Plan and for archive.  The LTWPF information is provided by WGRs to ERCOT and then archived for use in short term planning.

Figure 2 below depicts additional inputs to the wind power production forecasting service and the process that occurs within the service to generate the STWPF and the WGRPP forecasts.

Figure 2 Brief description: The Wind Power Production Forecast Service (WPPFS) shall ingest the regional weather data, WGR operational data, WGR specification data and WGR de-rating and scheduled outage data. A Quality Control (QC) procedure shall be applied to the WGR data and the regional weather data. WGR data inconsistencies identified by the QC module shall be reported to ERCOT. A 7-year archive of WGR data shall be maintained. The regional weather data and the WGR data shall be used to generate the STWPF and WGRPP forecasts through the use of physics-based and statistical atmospheric models as well as a WGR output model. A 7-year archive of WPPFS forecast data shall be maintained.

## Preconditions and Dependencies

ERCOT use of the STWPF hourly wind generation forecasts, LTWPF, and WGRPP forecasts depends on the following:

- Changes to the EMS database, registration process, and the Outage Scheduler to include the new operational and meteorological data

- Availability of specification data from registration and operational data from telemetry and plans from QSE’s

- An established communication plan between the QSE’s, ERCOT and the wind power production forecasting service

- Application changes to the EMS system to use the forecasts

# Functional Requirements

## Short Term Wind Production Forecast

| Requirement ID | RPP-FR1 |
| --- | --- |
| Requirement Name | Short Term Wind Production Forecast |
| Protocol Reference | Section(s) 3.13 (1) and 4.2.2 (1), TOP-002-1, IRO-005-1, TOP-006-0 |
| Coverage of Protocol | Partial and Full |
| Traceability to Sub-Process | COPS.P05.I-8, COPS.P05.I-9, COPS.P05.I-10, COPS.P05.P-3 |
| Sub-Process Element Coverage | Full |
| Description: The WPF process shall produce and update the STWPF (the expected value) hourly. Each forecast shall include hour-ending MW output, and probablility distribution of forecast error for the next 48 hours for each wind farm and the aggregate output of all wind farms. The following shall be used as inputs to the WPF process (see Table 1 for details): - Wind Farm specification data (from ERCOT registration) - Wind Farm operational data (from EMS) - Wind Farm scheduled availability (OS) - Forecasted and measured regional weather data (provided by vendor) |  |

## WGRPP Forecast

| Requirement ID | RPP-FR2 |
| --- | --- |
| Requirement Name |  |
| Protocol Reference | Section(s) 4.2.2 (2) and 4.2.2 (3) TOP-002-1, IRO-005-1, TOP-006-0 |
| Coverage of Protocol | Full and Full |
| Traceability to Sub-Process | COPS.P05.I-12 |
| Sub-Process Element Coverage | Full |
| Description: The WPF process shall produce and update a WGRPP, which is a hourly forecasted power production estimate that has an 80% probability of exceedance (i.e. 80% confidence level) from the STWPF. Each WGRPP forecast shall include an hour-ending MW value for the next 48 hours for each WGR and the aggregate of all WGR’s. |  |

## LTWPF Profiles

| Requirement ID | RPP-FR3 |
| --- | --- |
| Requirement Name | LTWPF Profiles |
| Protocol Reference | Section(s) 3.13 (2) TPL-005-0 |
| Coverage of Protocol | Partial |
| Traceability to Sub-Process | COPS.P05.I-13 |
| Sub-Process Element Coverage | Full |
| Description: The WPF process shall accept the LTWPF profiles from WGRs and provide this data to other applications. |  |

## WPF Data Posting

| Requirement ID | RPP-FR4 |
| --- | --- |
| Requirement Name | WPF Data Posting |
| Protocol Reference | Section(s) 3.9.1, 3.13 (1), 4.2.2 (4), 4.2.2 (5) |
| Coverage of Protocol | Partial, Full, Full |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The WPF process shall make available the following data to QSEs and for posting on the MIS: - STWPF for each WGR to each associated QSE (MIS Certified Area) - Aggregated STWPF for ERCOT (MIS Secured Area) - WGRPP for each WGR to each associated QSE (MIS Certified Area and Messaging System) - Aggregated WGRPP for ERCOT (MIS Secured Area) - Monthly metric performance as described in supplementary requirements SR5 and SR6 which demonstrate ERCOT’s objective criteria and thresholds for unbiased, accurate forecasts |  |

## Actual Wind Generation and Meteorological Data Archive

| Requirement ID | RPP-FR5 |
| --- | --- |
| Requirement Name | Actual Wind Generation and Meteorological Data Archive |
| Protocol Reference | Section(s) 17.3.1, 17.3.5 |
| Coverage of Protocol | Partial, Partial |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The vendor and ERCOT shall make available for archive the actual hourly wind generation and actual hourly meterological data used to develop the forecasts of each WGR site for at least 7 years. |  |

## WPF Forecasts Archive

| Requirement ID | RPP-FR6 |
| --- | --- |
| Requirement Name | WPF Forecasts Archive |
| Protocol Reference | Section(s) 17.3.1, 17.3.5 |
| Coverage of Protocol | Partial, Partial |
| Traceability to Sub-Process | None |
| Sub-Process Element Coverage | None |
| Description: The WPF process shall make available for archive all STWPF data, LTWPF data and WGRPP forecast data for at least 7 years. |  |

# Supplementary Requirements

## Availability Requirements

| Requirement ID | RPP-SR1 |
| --- | --- |
| Requirement Name | Forecast Availability for Day-Ahead Operations |
| Requirement Type | Availability |
| Description: At-least one valid, as defined in Data Validation requirements, WGRPP forecast for each Operating Day shall be available to ERCOT from the wind power production forecasting service, by 0600 of the Day-Ahead, 99.8% of the time, yearly. When it is not available by 0600, the wind power production forecasting service shall identify the condition, report to ERCOT, and with-in an hour produce forecast either by resolving the issues or generating an alternate forecast, for example from historical profiles. |  |

## Performance Requirements

| Requirement ID | RPP-SR2 |
| --- | --- |
| Requirement Name | Execution Time |
| Requirement Type | Performance |
| Description: For all WGRs and ERCOT, the execution of the following: Wind power modeling (performed by the wind power production forecasting service), the associated hourly wind generation forecasting (STWPF), and the hourly wind generation forecasting meeting the 80% confidence level (WGRPP) shall not take more than 15 minutes. |  |

| Requirement ID | RPP-SR3 |
| --- | --- |
| Requirement Name | Performance Metrics |
| Requirement Type | Performance |
| Description: The WPF Process shall calculate statistics comparing the forecasts to the actual total ERCOT wind-power output and the output of wind farms. These statistics shall include mean forecast, mean actual, mean error (bias), absolute mean error, RMS error, and a measure of dispersion (probably standard deviation) for total ERCOT wind-power production and each WGR for each hour-of-day by month for a set of specific forecast “lead times” (probably the 1600 forecast with a 8 hour lead time examinining the following day). |  |

## Forecast Accuracy Requirements

| Requirement ID | RPP-SR4 |
| --- | --- |
| Requirement Name | STWPF Forecast Accuracy |
| Requirement Type | Accuracy |
| Description: The STWPF shall meet the following accuracy criteria: - The absolute mean error shall be based on the maximum capacity of the WGR for the Day-Ahead forecast (the latest forecast prior to 0600 for all the hours in the next calendar day), over a calendar month. The absolute mean error is required to be less than 18%. |  |

| Requirement ID | RPP-SR5 |
| --- | --- |
| Requirement Name | WGRPP Forecast Accuracy |
| Requirement Type | Accuracy |
| Description: The WGRPP shall meet the following accuracy criteria: - The actual output of each WGR is less than the WGRPP produced in Day-Ahead, between 15% and 25% of the hours, over a calendar six month period. |  |

| Requirement ID | RPP-SR6 |
| --- | --- |
| Requirement Name | Wind Speed Forecast Accuracy |
| Requirement Type | Accuracy |
| Description: The wind speed forecast generated by the Wind Power Production Forecasting Service, the actual wind speed received from the WGR, and the wind speed forecast from an ERCOT designated vendor shall be compared. The Wind Power Production Forecasting Service vendor shall supply the generated wind speed forecasts to ERCOT. |  |

## STWPF Self-Training

| Requirement ID | RPP-SR7 |
| --- | --- |
| Requirement Name | Self Training |
| Requirement Type | Solution Methodology |
| Description: The vendors wind power production forecasting service shall support a STWPF self-training mode to train or re-train the Wind Power Model for each WGR based on the historical wind generation and meteorological data for each WGR site. |  |

## Data Validation

| Requirement ID | RPP-SR8 |
| --- | --- |
| Requirement Name | Forecast Validation |
| Requirement Type | Data Validation |
| Description: The output of WPF shall be validated to ensure that the forecasted MWh values are valid: that is they are non-negative and with in the maximum capability of each WGR. If the data is invalid, last valid forecast shall be provided, indicating the condition with a flag and potential reason. If no valid forecast is available to fall back on, then the forecast shall be provided from historical profiles. |  |

| Requirement ID | RPP-SR9 |
| --- | --- |
| Requirement Name | Handling Data Inconsistencies |
| Requirement Type | Data Validation |
| Description: The wind power production forecasting service will inform ERCOT of generation and WGR meteorological data errors within 2 business days. |  |

## Usability

| Requirement ID | RPP-SR10 |
| --- | --- |
| Requirement Name | WPF User Interface |
| Requirement Type | Usability |
| Description: ERCOT Operators shall have the capability to view WPF forecasts via a web browser. |  |

## Security

| Requirement ID | RPP-SR11 |
| --- | --- |
| Requirement Name | Communications Security |
| Requirement Type | Security |
| Description: All inbound communication from the wind power production forecasting service shall meet the following criteria: - Secure communication link - Authentication by digital certificate or other mutually agreed upon authentication mechanism - Data validation of input data to ERCOT systems |  |

# Protocol Coverage

| Protocol Sub-Section # (To the lowest level of granularity as possible) | Section Title | Coverage by Requirements (Full/Partial) | Covered by Requirement |
| --- | --- | --- | --- |
| 3.9.1 | Current Operating Plan (COP) Criteria | Partial | RPP-FR4 |
| 3.13 (1) | Renewable Production Potential Forecasts | Partial | RPP-FR1, RPP-FR4 |
| 3.13 (2) | Renewable Production Potential Forecasts | Partial | RPP-FR3 |
| 4.2.2 (1) | Wind-Powered Generation Resource Production Potential | Full | RPP-FR1 |
| 4.2.2 (2) | Wind-Powered Generation Resource Production Potential | Full | RPP-FR2 |
| 4.2.2 (3) | Wind-Powered Generation Resource Production Potential | Full | RPP-FR2 |
| 4.2.2 (4) | Wind-Powered Generation Resource Production Potential | Full | RPP-FR4 |
| 4.2.2 (5) | Wind-Powered Generation Resource Production Potential | Full | RPP-FR4 |
| 17.3.1 | Information System Data Collection and Retention | Partial | RPP-FR5, RPP-FR6 |
| 17.3.5 | Data Retention | Partial | RPP-FR5, RPP-FR6 |
| NERC TOP-002-1 | Normal Operations Planning | Partial | RPP-FR1 RPP-FR2 |
| NERC IRO-005-1 | Reliability Coordination — Current Day Operations | Partial | RPP-FR1 RPP-FR2 |
| NERC TOP-006-0 | Monitoring System Conditions | Partial | RPP-FR1 RPP-FR2 |
| NERC TPL-005-0 | Regional and Interregional Self-Assessment Reliability Reports | Partial | RPP-FR4 |