## Slide 1: Compliance Update
April 2007

## Slide 2: Control Performance Highlights
NERC CPS1 Performance
  Performance declined in February
    February performance comparison
      February 2007: 126.91
      February 2006: 141.06
    12 month rolling average comparison
      March 2006 February 2007: 141.47
      March 2005 February 2006: 127.97
PRR 525 Performance
  Initial scores for February indicate 32 QSEs passed / 1 non-wind-only QSE failed the measure
  Scores posted on the ERCOT Compliance Website
    SCE Performance Scores

## Slide 3: ERCOT CPS1 Performance Comparison

## Slide 4: ERCOT CPS1 by Interval

## Slide 5: QSE PRR525 10-Minute Interval Scoring

## Slide 6: February 2007 Resource Plan Performance Metrics

## Slide 7: 525 Passing 10-Min Interval Percentage Trends

## Slide 8: ERO / RE Activities
March 2nd: Latest draft of Entity Registration List submitted to NERC (work-in-progress)
April 2007: Anticipated that FERC will rule on Regional Delegation Agreements certifying the Texas RE to be the Regional Entity for the ERCOT Region
May 2007: Submit 1st draft of 2008 Texas RE Business Plan & Budget to NERC
June 2007: NERC Reliability Standards in place – mandatory compliance enforcement expected to begin

## Slide 9: October 3, 2006 Event Overview
Initiated at Gibbons Creek Substation in Bryan/College Station Area
  138 kV coupling capacitor voltage transformer (CCVT) failed catastrophically
  Current-sensing components of the backup protective relay failed due to high fault current
1,214 MW of generation lost – NERC Disturbance Control Standard (DCS) Event
  Frequency recovered to pre-disturbance level in approximately 3 minutes – NERC criteria met; no NERC Reliability Standards violation
339 MW of firm load shed in area

## Slide 10: October 3, 2006 Event Observations
LaaR Performance
  ERCOT deployed all RRS being provided by LaaRs in accordance with ERCOT DCS Event Operating Procedures.
  Six of ten QSEs with LaaR RRS awards did not respond with 95% of their award within 10 minutes.
    642 MW tripped – 1,150 MW obligation
    Took over 20 minutes to achieve 95% of obligation
  Seven Protocol Violation Notices issued.
    Six notices related to Section 6.5.4(2) – tripping requirements for LaaR
      1st occurrence – Constellation
      2nd occurrence – Formosa, Reliant, Suez, Tenaska, & Xtend (also had violations on April 17th)
    One notice related to Section 6.5.1.1(4) – telemetry requirements
      Xtend

## Slide 11: October 3, 2006 Event Observations
LaaR Performance
  QSEs receiving Protocol Violation Notices have substantially completed corrective actions.
  Currently, all requirements to perform apply to QSEs – should some be shifted to individual LaaR?
  PRR 714 Qualification and Periodic Testing of LaaR developed – tightens the requirements for initial qualification; introduces periodic testing requirements; and provides for more clearly defined conditions that would disqualify a LaaR for under/non-performance.

## Slide 12: October 3, 2006 Event Observations
Generator Trips
  Review of protective relay coordination of generators, per Operating Guides 3.1.4.6, requires TDSP input, as well as generator data – very technically demanding.
  Other related NERC and ERCOT requirements on protective relaying lack specificity but point out the need for review of relaying coordination between generators and TDSPs (for example, “…the protection scheme should be coordinated between the Generation Entity and the TDSP….).
  Generators need to perform mis-operations analysis – now a NERC requirement – but standards do not specify timeliness.

## Slide 13: October 3, 2006 Event Observations
Transmission Issues
  Work in progress to upgrade transmission protective relaying to current ERCOT Operating Guides which is required for new facilities only.
  Completing grid improvements planned in the area will reduce chances of reoccurrence. Scheduled completion by Summer 2008.
  Review switching responsibilities in Operating Guides for opportunities to clarify language. NERC Standards assign this responsibility to ERCOT as the registered NERC TOP.

## Slide 14: October 3, 2006 Event Observations
System Restoration
  Need to improve operations plans for switching and restoration by local companies in area. At least 7 TDSPs needed to work with each other and ERCOT.
  Need to improve internal communications to key facilities within TDSPs. Current requirements focus only on communications to ERCOT, not locally to facilities and local control centers.

## Slide 15: December 22, 2006 Event Overview
Initiated by fault in main power transformer at generating station
Local and remote generators tripped or reduced output ~1,900 MW.
Frequency spiked to 59.691 Hz. – LaaR automatically deployed (~830 MW); not all tripped. ERCOT issued instructions to QSEs to deploy remaining LaaR.
EECP Step 1 declared.
Event reported to NERC – generation loss exceeded amount required to qualify as a NERC DCS Event.
  Frequency recovered to pre-disturbance level in approximately 9 minutes

## Slide 16: December 22, 2006 Event Observations
Generator Trips
  Again, generators need to perform timely mis-operations analysis – NERC Standards do not specify this.
  Ride-through capability of generators during disturbances was reviewed, and this requires specific technical expertise and fault recorder information from TDSPs as well as generator owner input. It appears that some generation should not have tripped if Operating Guides requirements were met.
    Violation Notice issued to Generator Owner for non-compliance with an ERCOT Operating Guides Requirement – Operating Guide 3.1.4.6.

## Slide 17: December 22, 2006 Event Observations
LaaR performance
  Three Protocol Violation Notices issued.
    One notice related to Section 6.5.4(2) – tripping requirements for LaaR – Suez
    Two notices related to Section 6.5.1.1(4) – telemetry requirements – Tenaska & Xtend
    Required corrective actions in progress
  ERCOT Operations to ask for retest of certain LaaR under-frequency relays that did not trip automatically. No violations determined due to lack of high-speed frequency recordings at these locations and very short time that frequency dipped below 59.7 Hz. High speed frequency recorders in Austin may not be sufficient to validate frequency-triggered LaaR performance across the grid.