ERCOT Nodal Operating Guides

Section 8:  Telemetry and Communication

Draft (Month, Day, Year)

(Effective Upon Texas Nodal Market Implementation)

Contents

8	Telemetry and Communication	8-3

8.1  	Obligation	8-3

8.1.1	ERCOT Responsibilities	8-3

8.1.2	QSE and TSP Responsibilities	8-3

8.1.2.1	TSP and QSE Supplied Communications	8-4

8.1.3	QSE Use of Domain Name Service (DNS) or ERCOT Web-Based Front Page for Site Failover	8-5

8.1.3.1	DNS Server Configuration for Failover Support	8-5

8.1.3.2	Web-Based DNS Access	8-6

8.2	Communications	8-7

8.2.1	ERCOT WAN 	8-7

8.2.1.1	Metric of Availability	8-8

8.2.1.2	Maintenance and Restoration	8-8

8.2.2	ERCOT ICCP Interface	8-9

8.2.2.1     Quality Codes	8-9

8.2.2.1.1	ICCP Quality Codes from Market Participants to ERCOT	8-9

8.2.2.1.2	ICCP Quality Codes from ERCOT to Market Participants	8-11

8.2.2.2  Metric of Availability	8-12

8.3	Telemetry	8-12

8.3.1	Data from ERCOT to QSE’s	8-13

8.3.2	Data from ERCOT to TSP	8-13

8.3.3	Data from QSEs and TSPs to ERCOT	8-14

8.3.3.1	Weather Zone Data	8-14

8.3.4	TSP and QSE Telemetry Restoration	8-14

8.3.5	QSE and TSP Data Acquisition	8-15

8.3.6	General Telemetry Performance Criterion	8-15

8.3.6.1	Critically Important Telemetry Performance Criterion	8-15

8.4	Calibration and Testing of Telemetry	8-16

8.4.1	Responsibility	8-16

8.4.2	Test Equipment	8-16

8.4.3	Disputes	8-17

TSP

# Telemetry and Communication

#### 8.1  	Obligation

8.1.1	ERCOT Responsibilities

ERCOT supplies interface requirements, equipment, and installation for the entire ERCOT WAN, including equipment at each QSE and TSP control facility and back-up location, as well as ERCOT’s control centers.  ERCOT’s responsibilities include:

    - (a)	Supply and install fully configured and tested Customer Premises Equipment including routers, CSU/DSUs, LAN switch/hub and all support equipment for management purposes

    - (b)	Order and provision of local loop, network access point and transport;

    - (c)	Design, configure, test, and install network monitoring and management service;

    - (d)	Provide 24-hour network monitoring and management;

    - (e)	Provide 24X7 maintenance, with 4-hour response, for all ERCOT equipment located at participant site; and

    - (f)	ERCOT will maintain internal procedures to respond to all maintenance or performance issues within a specified timeframe; and

    - (g)	ERCOT will be the single point of contact for all network issues and will notify the reporting Market Participant and the ERCOT shift supervisor within 10 minutes of an issue being reported.  Two hour updates are required until the issue is resolved.

8.1.2	QSE and TSP Responsibilities

(1)	TSPs and QSEs whose facilities connect to the ERCOT WAN are required to sign an agreement with ERCOT governing installation, operation and maintenance.  Users of the ERCOT WAN shall provide signal connections, uninterruptible power, and physical space for ERCOT-supplied WAN interface equipment at their control centers, as well as 24-hour access for ERCOT installation and maintenance personnel.

(2)	At these facilities, computer and communications equipment connected to ERCOT WAN interfaces is the complete responsibility of the QSE or TSP.   Facilities shall have uninterruptible power supplies (UPS) capable of independently supplying all equipment connected to the ERCOT WAN for at least 72 hours.

(3)	Any TSP or QSE facility, whether primary or backup, involved in the transfer of the data sets identified in Attachment 9J, ERCOT Data Sets, will be required to connect directly to the ERCOT WAN Primary Private Network and Point-to-Point paths. If a TSP and QSE utilize the same EMS and server network at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TSP and QSE share a centralized PBX, separate OPX circuits will be terminated for each participant.  The Hotline will not be allowed to connect through the PBX system and is required for each participant.

(4)	A QSE or TSP involved in the transfer of the critical data identified in Attachment 9J, ERCOT Data Sets of these Operating Guides, will be required to provide the following communication resources to support the connection to the ERCOT private network:

  - (a)	Provide an analog business phone line or PBX analog extension for trouble-shooting and maintenance of equipment;

  - (b)	Provide a height of 24” of rack space in a 19” wide rack;

  - (c)	Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above;

  - (d)	Provide building wiring from circuit termination to equipment rack;

  - (e)	Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility;

  - (f)	Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors;

  - (g)	Provide on site personnel to escort ERCOT employees or contractors;

  - (h)	Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN;

  - (i)	Market Participant will be required to sign a security connection agreement with ERCOT;

  - (j)	Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site. Market Participants are responsible for their own security through this connection;

  - (k)	Provide a channel bank with at least one T1 interface, 4 FXS and two 4 wire analog ports. Connect FXS (e.g. PBX, key system) and 4 wire ports to the appropriate equipment.  On the digital T1 stream, levels for voice are zero dpm for transmit and receive;

  - (l)	Hotline must be a 500 set not attached to the Market Participant’s Phone System;

  - (m)	Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended; and

  - (n)	Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential.

(5)	A QSE or TSP not involved in the transfer of the data identified in Attachment 9J, ERCOT Data Sets of these Operating Guides, is not required to, but, may request ERCOT to provide an optional connection to the ERCOT private network.  When such a request is met by ERCOT, the QSE or TSP must then provide the above stated communications resources.

8.1.2.1		TSP and QSE Supplied Communications

(1)	Each TSP and QSE must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN.  For TSPs these include, but may not be limited to, voice communications and SCADA for substations and other Transmission Facilities.  For QSEs, these include, but may not be limited to, voice and SCADA for generating plants and loads.

(2)	QSEs and TSPs shall supply, implement and maintain all data and voice communication facilities required to fulfill the obligations set forth in these Operating Guides.

(3)	Proper performance, maintenance and testing of communication paths not directly connected to the ERCOT WAN shall be the responsibility of the TSP or QSE providing the path.

(4)	QSEs communicating with connected resources and TSPs communicating with substations are encouraged to use privately owned communication facilities.  Backup facilities utilizing common carriers, different privately owned facilities, or communications paths to a site are encouraged to provide increased reliability, i.e. separate paths to a site using different carrier, having multiple microwave paths leaving a site, etc.

### 8.1.3	QSE Use of Domain Name Service (DNS) or ERCOT Web-Based Front Page for Site Failover

A QSE possessing backup sites must utilize one of the following two options:

(a)	A WAN (Wide Area Network) Domain Name Service (DNS) server; or

(b)	An ERCOT provided web-based DNS service to facilitate the failover process when moving its operations between primary and backup sites.

The requirements of these options are specified below.

#### 8.1.3.1		DNS Server Configuration for Failover Support

(1)	A QSE is required to provide and maintain its own DNS servers that must be accessible by the ERCOT WAN.  The failover process requires the following:

(a)	DNS servers must support zone transfers over TCP port 53;

(b)	Firewalls must allow zone transfers to ERCOT DNS servers;

(c)	Zone files for the QSE's domains, e.g. www.examplepower.com, must reside on its WAN accessible DNS servers;

(d)	DNS servers must be set up as the master for its zone;

(e)	DNS servers must allow ERCOT DNS servers to transfer the zone files (ERCOT will be set up as a secondary/slave server for the zone);

(f)	The zone files must contain names for all local servers the QSE will need ERCOT services to access.  At a minimum, it must contain entries for the servers that can be switched over to the backup site.  The zone file must also contain entries for the QSE's primary website address, e.g. www.examplepower.com, and other common internet accessible sites that ERCOT servers may have occasional need to access; and

(g)	Time to Live (TTL) values for backup host entries in the zone file must be set to 0 in order to prevent the host to IP address mappings from being cached on the client machines.  This allows any changes made to a zone file to take effect immediately upon a zone transfer.

(2)	Once its DNS servers are operational, the QSE shall timely contact its ERCOT Client Services Representative and request that an ERCOT network administrator work with the QSE to test the functionality of the DNS setup.  The QSE must contact the ERCOT Client Services Representative at least five Business Days before testing.

(3)	After the zone transfer testing is complete, the QSE shall supply its ERCOT Client Services Representative with a list of participant servers, their DNS names, and their roles on the network.  The ERCOT Client Services Representative will then contact the application owners at ERCOT to change application communications to use the DNS name instead of IP addresses.

(4)	After successful completion of the test, when a QSE backup site failover is desired, the QSE shall update the zone file with its disaster recovery IP addresses and publish it to the ERCOT DNS servers.  The change will be effective immediately.  The QSE shall also implement a DNS server at its backup site.  This allows updated zone files to be published regardless if the primary site is up or not.

#### 8.1.3.2		Web-Based DNS Access

(1)	This access is provided as an alternative method for any QSE that does not wish to maintain its own DNS servers.  Access is provided over the ERCOT WAN only.  The QSE is responsible for access through its networks to the web servers located on the ERCOT WAN.  The QSE shall adhere to ERCOT password requirements.

(2)	To failover to or from a backup site, the QSE shall update the IP address of the existing entry.  ERCOT servers will accept the change and start using the new IP immediately.

(3)	Once the QSE has connectivity to the web server over the ERCOT WAN, it shall contact its ERCOT Client Services Representative and request that an ERCOT network administrator work with the QSE to test the functionality of the DNS setup.  The QSE shall contact the ERCOT Client Services Representative at least five Business Days before testing.  After testing is completed, the Client Services Representative will contact the application owners at ERCOT to change application communications to use DNS names instead of IP addresses.

(4)	After successful completion of the test, when a QSE site failover is desired, the QSE shall change the Web page entries with the active site information and the change will be effective immediately.

### 8.2	Communications

The following sections describe the communications standards of the wide area network (WAN) utilized for ICCP communications (Operational) and voice communications (Operational) that shall be used to exchange security and reliability information between:

(a)	ERCOT and a QSE; and

(b)	ERCOT and a TSP.

### 8.2.1	ERCOT WAN

ERCOT shall provide for a wide area network (ERCOT WAN) for secure communications path between ERCOT and the Market Participants in order to facilitate wholesale operations and frequency control as a single control area.  This communications network uses redundant, digital communications between ERCOT control centers and one or more facilities at each QSE and TSP.  The ERCOT WAN shall have sufficient bandwidth capacity and speed to enable:

(1)	Real-time (telemetry) data exchange for frequency control and transmission security;

(2)	Operational voice communications for both normal and emergency use.  The ERCOT WAN supports both off-premise exchanges (OPX) with ERCOT’s control facilities and the ERCOT hotlines; and

(3)	Data exchange to support applications programming interface (API) routines.  These include power scheduling, operating plans, outage requests, dispatch instructions, posting of information and other applications.

#### 8.2.1.1		Metric of Availability

ERCOT shall submit an annual report on the state of the WAN to the Market Participates. The report will include information about problems that we experienced during the year and ERCOT’s time frame in responding to these problems. ERCOT shall also classify the nature of the problems and has the problems were determined (i.e. reported by a Market Participate or ERCOT determined there was a problem using the monitoring tools that are required by this guide).

ERCOT shall also verify that an availability of the Communications path between each Market Participate an ERCOT achieved an availability of 99.999%.

8.2.1.2		Maintenance and Restoration

(1)	It is the joint responsibility of ERCOT WAN-connected Market Participants and ERCOT to coordinate maintenance and restoration activities so its reliability is not compromised.

(2)	All primary and back-up circuits shall be tested annually or as otherwise requested by ERCOT for end-to-end performance.

(3)	ERCOT will specify test procedures for hotline and any backup or alternate path voice circuits.

(4)	Test equipment to be used for the calibration or repair of communication equipment shall be certified to values of accuracy and precision.  The standard used for testing shall be superior to the tested equipment calibration requirements.

#### 8.2.2	ERCOT ICCP Interface

The Inter-Control Area Communications Protocol (ICCP) over the ERCOT WAN provides the real-time telemetry data from Market Participant computers, computer networks, or other devices.  Market Participants providing the data using an ICCP link must format their data and coordinate installation according to ERCOT procedures (ERCOT WAN Agreement).  The telemetry data furnished by a Market Participant’s ICCP link shall reflect the data quality codes of the individual data points as coordinated with ERCOT found in the Market Participant’s control computers and data collection system.  Market Participants shall provide documentation to ERCOT upon ERCOT’s request describing their control system quality codes and the mapping of their quality codes into the ERCOT defined quality codes.

8.2.2.1     Quality Codes

Status and analog telemetry data provided to ERCOT shall have the following associated quality codes:

(1)	“Valid” – represents analog or status data that the market participant and ERCOT considers valid;

(2)	“Suspect” - Any of the following: old value, old due to telemetry failure, considered suspect by the data owner, or otherwise should not be considered by ERCOT to be current.

(3)	“NOTVALID” – Value is invalid due to data acquisition/conversion errors or the initial value has never been established.

(4)	“Held” – Point has been taken off scan by Market Participant or otherwise removed from service.

Status and analog telemetry data provided to ERCOT shall have the following associated attributes:

(1)	“TELEMETERED” – Value was acquired from a field device.

(2)	“CALCULATED ” – Value is currently a calculated value and not estimated by a Market Participant State Estimator.

(3)	“ENTERED ” – represents analog or status data that is manually entered in the control system (not received from the field electronically).

(4)	“ESTIMATED” – Value was entered by a Market Participant’s State Estimator as an estimated value.

##### 8.2.2.1.1	ICCP Quality Codes from Market Participants to ERCOT

The following table describes the ICCP quality codes to be provided to ERCOT by the Market Participant.  The table includes:

(1)	The ICCP standard attribute name;

(2)	The ICCP standard named quality code of each attribute;

(3)	The conditions under which each ICCP quality code is to be set; and

(4)	A generic identifier of typical real-time database quality codes that would be mapped to the ICCP standard codes.

Table 1: ICCP Quality Codes from Market Participants to ERCOT

| ICCP Quality Attribute | ICCP Quality Code from Market Participant | Meaning | Generic RTDB Quality Code |
| --- | --- | --- | --- |
| Quality | VALID | Value is valid and can be trusted by ERCOT. | GOOD |
|  | HELD | Point has been taken off scan by Market Participant or otherwise removed from service. | NOT_IN_SERVICE |
|  | SUSPECT | Any of the following: old value, old due to telemetry failure, considered suspect by the data owner, or otherwise should not be considered by ERCOT to be current. | OLD (Stale) |
|  | NOTVALID | Value is invalid due to data acquisition/conversion errors or the initial value has never been established | BAD |
| Current Source | TELEMETERED | Value was acquired from a field device | REMOTE SOURCE |
|  | CALCULATED | Value is currently a calculated value and not estimated by a Market Participant State Estimator. | CALCULATED |
|  | ENTERED | Value was entered by a Market Participant operator. | MANUAL_ENTERED |
|  | ESTIMATED | Value was entered by a Market Participant’s State Estimator as an estimated value. | ESTIMATOR_ENTERED |
| Normal Value | NORMAL | The value is considered to be normal | (No special flag) |
|  | ABNORMAL | The value is considered to be abnormal | OFF_NORMAL |

##### 8.2.2.1.2	ICCP Quality Codes from ERCOT to Market Participants

The following table describes the ICCP quality codes to be provided to the Market Participant by the ERCOT, the conditions under which each ICCP quality code is set, and the translation from the local ERCOT real-time database quality codes to the related ICCP quality code.

Table 2:  ICCP Quality Codes from ERCOT to Market Participants

| ERCOT Local Quality Code | Meaning | ICCP Quality Code Sent to Market Participant | ICCP Quality Code |
| --- | --- | --- | --- |
| GOOD | Value is valid and can be trusted by Market Participant. | VALID | Quality |
| NOT_IN_SERVICE | Point has been taken off scan by ERCOT. | HELD |  |
| OLD (Stale) | Any of the following: old value, old due to telemetry failure, considered suspect by the original data owner, or otherwise should not be considered by Market Participant to be current. | SUSPECT |  |
| BAD OR UNINIT | Value is invalid due to data acquisition/conversion errors or the initial value has never been established | NOTVALID |  |
| NREMOTE | Value was acquired from a field device by the data owner. ERCOT is passing this information on to the Market Participant. | TELEMETERED | Current Source |
| NCALC AND NOT REPLACED | Value is currently a calculated value by ERCOT and not estimated by SE. | CALCULATED |  |
| MANREP | Value was manually entered either by the ERCOT operator or by the data owner | ENTERED |  |
| ESTREP | Value was entered by the ERCOT State Estimator as an estimated value. | ESTIMATED |  |
| NOT ABNORMAL | The value is considered to be normal by ERCOT per ERCOT’s database configuration | NORMAL | Normal Value |
| ABNORMAL | The value is considered to be abnormal by ERCOT per ERCOT’s database configuration | ABNORMAL |  |

8.2.2.2  	Metric of Availability

(1)	ICCP links must achieve a monthly availability of 98%, excluding approved Planned Outages.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data.  A link will be considered as available when at least 85% of the data defined on that link is successfully transferred to ERCOT with a “Valid” or “Held and Entered” quality code.  This will include establishing a process to coordinate downtime for ICCP links and database maintenance.

(2)	ICCP links shall use fully redundant data communication from the QSE and TSP control systems to the ERCOT System such that any single element of the communication system can fail and:

(a)	For server failures, complete real-time data transfer must be re-established within five minutes by automatic failover to alternate server(s); and

(b)	For all communication failures, complete real-time data transfer must continue to flow from the QSE and TSP control systems to the ERCOT System with updates of all data continuing at a 30 second or less scan rate.

#### 8.3	Telemetry

#### (1)	QSE control centers required to supply real-time telemetry data to ERCOT shall use an Inter-Control Area Communications Protocol (ICCP) interface through the ERCOT WAN.  QSEs shall also receive signals from ERCOT over the ICCP interface to implement frequency control.

(2)	TSP control centers required to supply real-time telemetry data to ERCOT shall use an ICCP interface through the ERCOT WAN.

(3)	Each QSE and/or TSP shall continuously provide to ERCOT the telemetry data quantities that they are responsible for.  The frequency of update, means of communication to ERCOT, and format for each point provided by each Entity shall follow the specifications in Attachment 9J, ERCOT Data Sets for that entity, unless otherwise specified by ERCOT.  At the frequency specified in the Attachment 9J, ERCOT Data Sets, each update cycle shall provide new readings of all data points being monitored, not averages linked to prior cycle readings or repetition of readings from a previous cycle.  Design accuracy and availability of data points delivered to ERCOT shall satisfy the requirements and standards for telemetry performance and State Estimator performance as specified under Section 8.1.6, Data from QSEs and TSPs to ERCOT.

(4)	QSEs, Resources and TSPs are required to provide power operation data to ERCOT including, but not limited to:

- (a)	Real time generation data from QSEs;

- (b)	Planned Outage information from Resources;

- (c)	Transmission system network data used by any TSP’s control center, including:

  - (i)	Breaker and line switch status of all ERCOT Transmission Elements;

  - (ii)	Line flow MW and MVAR;

  - (iii)	Breaker, switches connected to all Resources;

  - (iv)	Transmission Facility Voltages; and

  - (v)	Transformer MW, MVAR and TAP.

- (d)	Real time generation and Load Resource telemetry  data from QSEs;

- (e)	Real time Generation meter splitting telemetry data from QSEs;

- (f)	Planned Transmission Outage information from TSPs;

- (g)	Transmission system network model data including constraints) from TSPs;

- (h)	Current Operating Plans from QSEs; and

- (i)	Dynamic Schedules from QSEs.

(5)	Real-Time telemetry data provided to ERCOT shall be at the same scan rate that the TSP or QSE control computers and data collection system obtains the data from telemetry.

#### 8.3.1	Data from ERCOT to QSE’s

ERCOT shall provide all required data to QSE’s in accordance with the Operating Guide and the Protocols.  Attachment 9J, ERCOT Data Sets provides the informational data sets that ERCOT will send to the QSEs.

#### 8.3.2	Data from ERCOT to TSP

(1)	ERCOT shall provide operational data and issue instructions to the TSP in accordance with the Operating Guide and the Protocols.

(2)	ERCOT is required to provide the following power operation data to TSPs for the purpose of providing reliability information as determined by ERCOT:

        - (a)	Status of any breakers and switches in ERCOT's Real-Time data base;

        - (b)	State Estimator solutions;

        - (c)	Transmission line flows and voltages;

        - (d)	Transformer information;

        - (e)	QSE Resource data; and

        - (f)	Voltage schedules at transmission busses.

(3)	ERCOT will give notice to the Entities supplying the above list of data to ERCOT upon the initial provision of such data to the TSP.

#### 8.3.3	Data from QSEs and TSPs to ERCOT

(1)		QSEs and TSPs shall provide Real-Time monitoring of power system quantities to ERCOT as defined in the Operating Guides and Protocols.  Attachment 9J of this Operating Guide specifies the format and description for the content of each type of data point that ERCOT may request from TSPs and QSEs.  Not all data points in Attachment 9J are required from each Entity.  ERCOT shall work with TSPs and QSEs to determine the required data using the methodology presented in the Protocols.   At a minimum, all the device status and analog measurements that the TSPs and QSEs use to operate their facilities shall be provided.    Ultimately, it is the responsibility of the TSPs and QSEs to provide all data requested by ERCOT as set forth in the Protocols and Operating Guides.

(2)	Real-Time telemetry data from QSEs used to supply power or Ancillary Services shall be integrated by ERCOT and checked against settlement meter values on a monthly basis.

(3)	Where multiple generators share a single net settlement meter, the ratio of integrated Real-Time data from each generator shall be used to proportion the total settlement quantity.

(4) 	Each QSE and TSP should Notify ERCOT when telemetry being provided will not be available or reliable for operations purposes. When ERCOT receives prior notification these points should be removed from the any performance metrics calculations.

#### 8.3.3.1		Weather Zone Data

(1)	A TSP that is responsible for providing Weather Zone tie-line measurement data to ERCOT is required to establish a backup to the primary source.

(2)	TSPs having an EMS with a native ICCP application capable of four second periodic data set transfers with minimum 300 points per data set, and hot standby backup ICCP servers with automatic fail-over capability, shall provide an additional ICCP association across the ERCOT WAN for the transfer of Weather Zone tie line measurements.  ICCP nodes should exist at primary and backup facilities.

8.3.4	TSP and QSE Telemetry Restoration

Real-time telemetry data shall be provided continuously.  Data that is inaccurate or of bad quality, whether failed or in error, must be restored promptly by the provider of the telemetry data.  It is recognized that some data may be of more importance than other data.  ERCOT will inform the TSP or QSE of data in this category that needs to be repaired to service as quickly as possible.  QSEs and TSPs shall provide information to ERCOT of any and all corrective actions taken to restore reported telemetry errors to ERCOT upon request.  When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, take corrective action to either:

(a)	Calibrate/repair the mis-behaving equipment;

(b)	Request an outage to schedule calibration/repair of the mis-behaving equipment;

(c)	Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame; or

(d) 	Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.

Before ERCOT requests review/re-calibration of a telemetry problem with a piece of equipment it shall discuss the problem with the provider to attempt to arrive at a consensus decision for the most appropriate action.

8.3.5	QSE and TSP Data Acquisition

Suppliers of Real-Time telemetry must collect and process telemetry data from field equipment at their control centers before passing to the ERCOT interface.  The equipment and processes are owned and operated entirely by the supplier.  Traditionally, utilities have used both analog and digital methods of transmission at existing facilities.  It is the responsibility of the QSEs and TSPs who supply other Entities’ data to ERCOT to also arrange for reliable delivery of telemetry data from the field equipment from the other entities in order to support the requirements in these Operating Guides.

### 8.3.6	General Telemetry Performance Criterion

The following criteria will apply to Real-Time telemetry provided to ERCOT:

(1)	The TSP shall maintain the sum of flows into any telemetered bus less than the greater of 5 MW or 5% of the largest line rating at each bus.

(2)	Each QSE or TSP shall provide telemetry data to ERCOT such 98% of all telemetry provided to ERCOT achieves a quarterly availability of at least 80% percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with good quality codes at the scheduled periodicity.

(3)	Exceptions to the general telemetry performance criterion shall be made for data points that do not have a market impact in the quality of the State Estimator solution or required for the reliable operation of the ERCOT Transmission Facilities  Some examples of these are:

  - (a)	Substation with no more than two transmission lines and less than 10 MW of load;

  - (b)	Connection of Loads along a continuous, non-branching circuit that may be combined for telemetry purposes;

  - (c)	Substations connected radially to the bulk transmission system.

### 8.3.6.1	Critically Important Telemetry Performance Criterion

(1)	ERCOT shall create a list of those MW/MVAR telemetry pairs, not exceeding 10% of the Transmission Elements in ERCOT, and up to 20 voltage points that are identified as critically important to reliability, system observability, support of State Estimator performance, or are of a commercial Market concern. This list of critically important telemetry must meet more stringent criteria for accuracy and availability where specifically addressed. ERCOT shall review and publish this list annually. ERCOT shall use the following criteria to identify critically important telemetry:

(a)	Loss of telemetry points that result in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(b)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(c)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on transmission facilities designated as critically important to transmission reliability by ERCOT. A list of these critical facilities will be published annually.

(d)	Telemetry necessary to monitor transmission elements identified as causing 80% of congestion cost in the year for which the most recent data is available.

(e)	Telemetry necessary to monitor the 20 most voltage critical buses designated by ERCOT and approved by TAC each October.

(2)	Each QSE or TSP shall provide identified critical telemetry data to ERCOT such that 95% percent of the critically important telemetry identified by ERCOT must achieve a quarterly availability of at least 90% percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with “Valid” or “Held and Entered” quality codes at the scheduled periodicity.

### 8.4	Calibration and Testing of Telemetry

8.4.1	Responsibility

It is the responsibility of the owner of telemetry equipment to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds that which is specified in the ERCOT Protocols and these Operating Guides, for both the overall system and for individual equipment.  Coordination of calibration and testing activities with ERCOT is also the responsibility of the owner.  Upon ERCOT’s request, each TSP and QSE shall provide ERCOT access to its preventive maintenance and calibration test procedures and records for purposes of ensuring accurate telemetry of data.   If a TSP and/or QSE repeatedly fails other telemetry metrics defined in these Operating Guides, ERCOT may require the owner to revise its procedures to ensure accuracy and availability of telemetry data.

8.4.2	Test Equipment

Test equipment and to be used for the calibration or repair of telemetry and associated equipment shall be certified to values of accuracy and precision. The standard used for testing shall be superior to the tested equipment calibration requirements.

8.4.3	Disputes

Where a dispute over the accuracy or performance of any telemetry equipment exists, ERCOT may request a comparison of accuracy and/or a joint calibration of affected equipment.

# Comments

8.1.2

8.1.3

Security, Facilities, and Connectivity Requirements of WAN Systems - put in Appendix - Send to Jim Brenton to review - 8.3.3 Step 4.  Consistency with NERC Requirements - see Vann Weldon.

Table

Should be deleted because it is redundant with 8.3.3.

8.1.3

8.1.4 - see outline

8.1.4.1 - see outline

parentheses use

8.1.4.2

8.1 - see outline - need to add more verbage to make it an introduction

parentheses use

8.2.1 - see outline

parentheses use

8.1.1

Come back to this statment - issues with liability, affected companies, etc.

Parenthese use - location of agreement on the ERCOT MIS?

Not defined or acronym

Spell Out?

Check Section Reference

Need additional review – should this be more generically referenced as “critical data”?

Spell out - not an acronym

Where do these standards reside?  ERCOT MIS?

parentheses use is incorrect/confusing

Not an acronym - spell out

In the TAC-approved Telemetry Standards

not a defined term

No relevance in the Nodal Market

Redundant

parenthese use

Move to Section 9

Waiting for PRR 647 to pass

Waiting for PRR 647 to pass