From: 	<Sherry.Looney@txu.com>

To:	<Jack.Thormahlen@lcra.org>

Date: 	4/3/2007 10:16:06 AM

Subject: 	RE: OGRTF Comments on OGRR192

Jack,

It is possible that simple cycle CT's which are used primarily for

non-spin may not be online at the start of any underfrequency events

within a two year period.  They are often brought online after the

initial event has occurred so that the data required for the proof by

historical data will not be available.

Companies whose CT's are not able to conduct the online test will have

to apply for an exemption if their units are not online at the time an

underfrequency event occurs or develop an offline test.

Therefore, TXU recommends a remand by ROS to look at additional

language.

Thanks,

Sherry Looney

-----Original Message-----

From: Jack Thormahlen [mailto:Jack.Thormahlen@lcra.org]

Sent: Tuesday, April 03, 2007 9:53 AM

To: Looney, Sherry

Cc: Bob Green; Sydney Niemeyer

Subject: RE: OGRTF Comments on OGRR192

Sherry - I am presuming that you are recommending a remand by ROS to

look at additional language or have a written procedure for an off-line

test as Tenaska has commented. Is this a correct reading on my part? As

you may remember, the OGRTF has invited the Market Participants that can

not do an on-line test and are not on line during a system frequency

event, to write an off-line test procedure. The PDCWG is the initiator

or this OGRR. They believe that all combustion turbines need to be

tested and not exempted. It will be a rare case that a combustion

turbine will not be on line during a system frequency event that is

reviewed by the PDCWG during a given two year period that droop testing

is required.

>>> <Sherry.Looney@txu.com> 4/3/2007 9:24 AM >>>

My comments:

Add language to clarify that if a unit is not capable of conducting the

online test due to the possibility of equipment damage, the unit will be

exempt from testing if it is not online at the time of a frequency

disturbance event within the two year time for testing.

Thanks,

Sherry Looney

-----Original Message-----

From: Jack Thormahlen [mailto:Jack.Thormahlen@lcra.org]

Sent: Tuesday, April 03, 2007 9:20 AM

To: Looney, Sherry

Subject: RE: OGRTF Comments on OGRR192

Steve's father-in-law had a second heart attack last weekend and Steve

has not been in the office to forward your response to me. Please resend

the response to me for my use in the tally of responses.

Thanks

Jack Thormahlen, P.E.

LCRA

Sr. Power System Analyst

1-800-776-5272 ext.2635

Thanks

Jack Thormahlen, P.E.

LCRA

Sr. Power System Analyst

1-800-776-5272 ext.2635

>>> <Sherry.Looney@txu.com> 4/3/2007 8:51 AM >>>

I sent my comments to Steve Knapp the day the email went out.

Thanks,

Sherry

-----Original Message-----

From: Jack Thormahlen [mailto:Jack.Thormahlen@lcra.org]

Sent: Friday, March 30, 2007 10:53 AM

To: ERCOT Operations Working Group

Subject: Fwd: OGRTF Comments on OGRR192

As promised - This email is for the purpose of obtaining consensus from

the OWG to forward the OGRR192 (attached) as the recommendation of OWG

to ROS. This is with the proviso that an additional OGRR will be

produced by Tenaska and/or TXU or anyone else that cares to submit the

test procedure, that provides for an off-line test procedure. Please

respond to this email with your desire to have the attached OGRR192

revision as the OWG recommendation to ROS by stating YES or by stating

NO. If NO, please provide the reason. If, YES is a consensus, then Ann

and I will officially make the document reflect this response. I look

forward to your quick response by EOB Monday, April 2, 2007.

Thanks

Jack Thormahlen, P.E.

LCRA

Sr. Power System Analyst

1-800-776-5272 ext.2635