## Beta Results
MP | Station | TSP | QSE | Metrics | # of Points Checked | # of Points to Check | % of Points Checked | Total Minutes to Complete | Average Minutes to Complete per Point | ERCOT Error Detail | Missing Equipment on Network Model | Missing Points | Mis-Mapped Points | Quality Code Issue - Field Telemeter | Quality Code Issue - Not Field Telemeter | Polarity Reversed | Point not Directly Routed to ERCOT | ERCOT Error SUMMARY | ERCOT # of Errors Found | % of ERCOT Non-Quality Code Errors | TOTAL % of ERCOT Errors
AEN - Austin Energy | Onion | x |  |  | 32 | 32 | 100% | 28 | 0.875 |  | 0 | 0 | 0 | 0 | 0 | 3 | 0 |  | 3 | 9.375% | 9.375%
| McNeil | x |  |  | 74 | 74 | 100% | 46 | 0.62162 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| Decker |  | x |  | 30 | 30 | 100% | 85 | 2.8333 |  | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 6 | 0% | 20%
| Holly |  | x |  | 12 | 12 | 100% | 41 | 3.4167 |  | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4 | 0% | 33.33%
AEP - American Electric Power | Nedin | x |  |  | 181 | 181 | 100% | 160 | 0.88398 |  | 2 | 0 | 4 | 0 | 82 | 0 | 0 |  | 88 | 3.315% | 48.62%
| Riohondo | x |  |  | 88 | 88 | 100% | 101 | 1.1477 |  | 0 | 1 | 2 | 1 | 44 | 0 | 0 |  | 48 | 3.409% | 54.55%
| No test |  | x |  | 0 | 20 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| No test |  | x |  | 0 | 20 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
APX | BYU |  | x |  | 28 | 28 | 100% | 7 | 0.25 |  | 0 | 4 | 4 | 0 | 0 | 0 | 0 |  | 8 | 28.57% | 28.57%
| Haysen |  | x |  | 24 | 24 | 100% | 23 | 0.95833 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| MDANP |  | x |  | 12 | 12 | 100% | 7 | 0.58333 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 2 | 16.67% | 16.67%
BEC - Brazos Electric Coop | Jackcnty | x | x |  | 46 | 46 | 100% | 90 | 1.9565 |  | 0 | 2 | 0 | 14 | 0 | 0 | 0 |  | 16 | 4.348% | 34.78%
| Mil | x | x |  | 51 | 51 | 100% | 90 | 1.7647 |  | 3 | 0 | 0 | 26 | 0 | 0 | 0 |  | 29 | 5.882% | 56.86%
BTU - Bryan Texas Utilities | Dansby | x | x |  | 36 | 36 | 100% | 99 | 2.75 |  | 1 | 0 | 2 | 0 | 0 | 0 | 3 |  | 6 | 16.67% | 16.67%
Calpine Power Management | Duke |  | x |  | 24 | 24 | 100% | 103 | 4.2917 |  | 0 | 0 | 0 | 8 | 0 | 0 | 0 |  | 8 | 0% | 33.33%
| Nedin |  | x |  | 17 | 17 | 100% | 73 | 4.2941 |  | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 6 | 0% | 35.29%
Constellation Energy | WHCCS |  | x |  | 18 | 18 | 100% | 23 | 1.2778 |  | 0 | 0 | 0 | 18 | 0 | 0 | 0 |  | 18 | 0% | 100%
| FLCNS |  | x |  | 15 | 15 | 100% | 22 | 1.4667 |  | 0 | 0 | 0 | 15 | 0 | 0 | 0 |  | 15 | 0% | 100%
Coral Power | TGCCS |  | x |  | 30 | 30 | 100% | 41 | 1.3667 |  | 0 | 0 | 1 | 29 | 0 | 0 | 0 |  | 30 | 3.333% | 100%
CPE - CenterPoint Energy | Green Bay | x |  |  | 149 | 149 | 100% | 265 | 1.7785 |  | 0 | 0 | 13 | 6 | 32 | 0 | 0 |  | 51 | 8.725% | 34.23%
| O'Brien | x |  |  | 78 | 78 | 100% | 97 | 1.2436 |  | 0 | 0 | 0 | 0 | 18 | 0 | 0 |  | 18 | 0% | 23.08%
CPS - City Public Services | Braunig | x |  |  | 86 | 86 | 100% | 43 | 0.5 |  | 0 | 38 | 0 | 0 | 0 | 0 | 0 |  | 38 | 44.19% | 44.19%
| Leon Crk | x |  |  | 87 | 87 | 100% | 80 | 0.91954 |  | 0 | 30 | 4 | 0 | 0 | 0 | 0 |  | 34 | 39.08% | 39.08%
| Leon Crk |  | x |  | 6 | 6 | 100% | 84 | 14 |  | 0 | 0 | 0 | 6 | 0 | 0 | 0 |  | 6 | 0% | 100%
| Calavers |  | x |  | 4 | 4 | 100% | 7 | 1.75 |  | 0 | 0 | 0 | 4 | 0 | 0 | 0 |  | 4 | 0% | 100%
Denton Municipal Electric | Teasly | x |  |  | 10 | 10 | 100% | 6 | 0.6 |  | 0 | 0 | 0 | 0 | 1 | 0 | 0 |  | 1 | 0% | 10%
| Woodrow | x |  |  | 14 | 14 | 100% | 12 | 0.85714 |  | 0 | 0 | 0 | 0 | 0 | 4 | 0 |  | 4 | 28.57% | 28.57%
Dynergy | Not in Nodal |  | x |  | 0 | 0 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| Not in Nodal |  | x |  | 0 | 0 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Exelon | Handley |  | x |  | 33 | 33 | 100% | 0 | 0 |  | 0 | 4 | 0 | 29 | 0 | 0 | 0 |  | 33 | 12.12% | 100%
| MCSES |  | x |  | 36 | 36 | 100% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
FPL | Lpccs |  | x |  | 43 | 43 | 100% | 55 | 1.2791 |  | 0 | 0 | 15 | 0 | 0 | 0 | 0 |  | 15 | 34.88% | 34.88%
| Rdcanyon |  | x |  | 5 | 5 | 100% | 5 | 1 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Garland Power and Light | Brand C | x |  |  | 24 | 24 | 100% | 43 | 1.7917 |  | 0 | 0 | 0 | 0 | 11 | 0 | 0 |  | 11 | 0% | 45.83%
| Olinger | x | x |  | 72 | 72 | 100% | 53 | 0.73611 |  | 0 | 0 | 0 | 0 | 28 | 0 | 0 |  | 28 | 0% | 38.89%
GEUS - Greenville | Steam | x | x |  | 16 | 16 | 100% | 78 | 4.875 |  | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  | 3 | 18.75% | 18.75%
LCRA - Lower Colorado River | Gideon | x |  |  | 79 | 79 | 100% | 120 | 1.519 |  | 0 | 0 | 1 | 0 | 47 | 0 | 0 |  | 79 | 1.266% | 100%
| Lostpi | x |  |  | 10 | 10 | 100% | 20 | 2 |  | 0 | 0 | 0 | 0 | 10 | 0 | 0 |  | 10 | 0% | 100%
| Gideon |  | x |  | 21 | 21 | 100% | 40 | 1.9048 |  | 0 | 0 | 2 | 19 | 0 | 0 | 0 |  | 21 | 9.524% | 100%
| Lostpi |  | x |  | 21 | 21 | 100% | 40 | 1.9048 |  | 0 | 0 | 0 | 21 | 0 | 0 | 0 |  | 21 | 0% | 100%
Mirant Energy | No test |  | x |  | 0 | 20 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| No test |  | x |  | 0 | 20 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
NRG | CBY |  | x |  | 10 | 10 | 100% | 30 | 3 |  | 1 | 0 | 0 | 2 | 0 | 0 | 0 |  | 3 | 10% | 30%
| WAP |  | x |  | 44 | 44 | 100% | 95 | 2.1591 |  | 0 | 0 | 0 | 9 | 0 | 0 | 0 |  | 9 | 0% | 20.45%
Occidental Power Services | Inglcosw |  | x |  | 24 | 24 | 100% | 112 | 4.6667 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 25% | 25%
| DIB |  | x |  | 30 | 30 | 100% | 83 | 2.7667 |  | 6 | 0 | 0 | 0 | 0 | 0 | 0 |  | 6 | 20% | 20%
PUB - Brownsville Public Utilities | Loma Alt | x |  |  | 15 | 15 | 100% | 5 | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 15 |  | 15 | 100% | 100%
| Silasray | x |  |  | 17 | 17 | 100% | 14 | 0.82353 |  | 0 | 0 | 0 | 0 | 0 | 0 | 17 |  | 17 | 100% | 100%
Reliant | Channel Vw |  | x |  | 28 | 28 | 100% | 39 | 1.3929 |  | 0 | 0 | 4 | 24 | 0 | 0 | 0 |  | 28 | 14.29% | 100%
| Terso |  | x |  | 4 | 4 | 100% | 15 | 3.75 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
RCEC - Rayburn County Electric | No test | x |  |  | 0 | 40 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| No test | x |  |  | 0 | 40 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
STEC - South Texas Electric Coop | Pearsall | x | x |  | 89 | 89 | 100% | 129 | 1.4494 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 2 | 2.247% | 2.247%
| Sanmigl | x |  |  | 49 | 49 | 100% | 29 | 0.59184 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| Sanmigl |  | x |  | 6 | 6 | 100% | 17 | 2.8333 |  | 0 | 0 | 3 | 0 | 0 | 0 | 0 |  | 3 | 50% | 50%
Suez Energy Marketing | ETCCS |  | x |  | 15 | 15 | 100% | 11 | 0.73333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| WCPP |  | x |  | 21 | 21 | 100% | 6 | 0.28571 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Tenaska Power Services | Basten |  | x |  | 18 | 18 | 100% | 10 | 0.55556 |  | 0 | 0 | 6 | 0 | 0 | 0 | 0 |  | 6 | 33.33% | 33.33%
| Braz_wnd |  | x |  | 7 | 7 | 100% | 15 | 2.1429 |  | 0 | 2 | 2 | 0 | 0 | 0 | 0 |  | 4 | 57.14% | 57.14%
| Formosa |  | x |  | 64 | 64 | 100% | 58 | 0.90625 |  | 0 | 0 | 5 | 0 | 0 | 0 | 0 |  | 5 | 7.812% | 7.812%
| Rionog |  | x |  | 20 | 20 | 100% | 25 | 1.25 |  | 0 | 0 | 4 | 0 | 0 | 0 | 0 |  | 4 | 20% | 20%
| Sweetwnd |  | x |  | 7 | 7 | 100% | 6 | 0.85714 |  | 0 | 0 | 2 | 0 | 0 | 0 | 0 |  | 2 | 28.57% | 28.57%
| Silasray |  | x |  | 37 | 37 | 100% | 40 | 1.0811 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TMPA - Texas Muni Power Auth | GN_S_I | x |  |  | 20 | 20 | 100% | 30 | 1.5 |  | 0 | 0 | 1 | 0 | 4 | 0 | 0 |  | 5 | 5% | 25%
| Garland** | x |  |  | 0 | 0 | 100% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TNMP - Texas New Mex Power | No test | x |  |  | 0 | 40 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| No test | x |  |  | 0 | 40 | 0% | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TXU - Texas Utilities | JAX | x |  |  | 21 | 21 | 100% | 7 | 0.33333 |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| Jewett | x |  |  | 102 | 102 | 100% | 47 | 0.46078 |  | 1 | 0 | 0 | 0 | 0 | 0 | 0 |  | 1 | 0.9804% | 0.9804%
| Emses |  | x |  | 18 | 18 | 100% | 39 | 2.1667 |  | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 3 | 0% | 16.67%
| Nlses |  | x |  | 18 | 18 | 100% | 50 | 2.7778 |  | 0 | 0 | 0 | 3 | 0 | 0 | 0 |  | 3 | 0% | 16.67%
TOTAL |  |  |  | 0 | 2196 | 2436 | 90.15% | 2999 | 1.3657 |  | 20 | 81 | 82 | 253 | 277 | 7 | 35 |  | 755 | 10.25% | 34.38%
** Garland operates Greenville and TMPA - their testing has covered these stations

## ICCP Results
MP | TSP | QSE | Verify | MP Server Failure <= 5 minute recovery | MP Other Failure <= 30 second recovery | TEST Completed
AEN - Austin Energy | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
AEP - American Electric Power | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
APX |  | x |  |  |  | 0%
BEC - Brazos Electric Coop | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
BTU - Bryan Texas Utilities | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
Calpine Power Management |  | x |  |  |  | 0%
Constellation Energy |  | x |  |  |  | 0%
Coral Power |  | x |  |  |  | 0%
CPE - CenterPoint Energy | x |  |  |  |  | 0%
CPS - City Public Services | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
Denton Municipal Electric | x |  |  |  |  | 0%
Dynergy |  | x |  |  |  | 0%
Exelon |  | x |  |  |  | 0%
FPL |  | x |  |  |  | 0%
Garland Power and Light | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
GEUS - Greenville | x |  |  |  |  | 0%
LCRA - Lower Colorado River | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
Mirant Energy |  | x |  |  |  | 0%
NRG |  | x |  |  |  | 0%
Occidental Power Services |  | x |  |  |  | 0%
PUB - Brownsville Public Utilities | x |  |  |  |  | 0%
Reliant |  | x |  |  |  | 0%
RCEC - Rayburn County Electric | x |  |  |  |  | 0%
STEC - South Texas Electric Coop | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
Suez Energy Marketing |  | x |  |  |  | 0%
Tenaska Power Services |  | x |  |  |  | 0%
TMPA - Texas Muni Power Auth | x |  |  |  |  | 0%
TNMP - Texas New Mexico Pow | x |  |  |  |  | 0%
TXU - Texas Utilities | x |  |  |  |  | 0%
|  | x |  |  |  | 0%
TOTAL |  |  | 0 |  |  | #REF!

## P2P Estimates
MP | TSP | QSE | Estimating Metrics | Station Count | Existing Point Count (Zonal based) | Unit Resource Count (QSEs only) | Additional Unit Resource Points (30 new per) | Load Resource Count (QSEs only) | Additional Load Resource Points (30 new per) | New Point Count (Nodal based) | Estimated Duration | Minutes per Point to Verify (Beta Results) | Estimated Hours | Average Working Hours per Week | Estimated Weeks | Estimated Days
AEN - Austin Energy | x |  |  | 61 | 2042 |  |  |  |  | 2042 |  | 1 | 34.0333 | 35 | 0.97238 | 4.8619
|  | x |  | 7 | 572 | 21 | 630 | 4 | 120 | 1322 |  | 1 | 22.0333 | 35 | 0.62952 | 3.1476
AEP - American Electric Power | x |  |  | 683 | 10932 |  |  |  |  | 10932 |  | 1 | 182.2 | 35 | 5.2057 | 26.0286
|  | x |  | 6 | 334 | 9 | 270 | 3 | 90 | 694 |  | 1 | 11.5667 | 35 | 0.33048 | 1.6524
APX |  | x |  | 15 | 1122 | 58 | 1740 | 11 | 330 | 3192 |  | 1 | 53.2 | 35 | 1.52 | 7.6
BEC - Brazos Electric Coop | x |  |  | 318 | 4169 |  |  |  |  | 4169 |  | 1 | 69.4833 | 35 | 1.9852 | 9.9262
|  | x |  | 7 | 307 | 13 | 390 | 2 | 60 | 757 |  | 1 | 12.6167 | 35 | 0.36048 | 1.8024
BTU - Bryan Texas Utilities | x |  |  | 19 | 311 |  |  |  |  | 311 |  | 1 | 5.1833 | 35 | 0.1481 | 0.74048
|  | x |  | 7 | 505 | 18 | 540 | 4 | 120 | 1165 |  | 1 | 19.4167 | 35 | 0.55476 | 2.7738
Calpine Power Management |  | x |  | 13 | 821 | 44 | 1320 | 14 | 420 | 2561 |  | 1 | 42.6833 | 35 | 1.2195 | 6.0976
Constellation Energy |  | x |  | 2 | 107 | 6 | 180 | 0 | 0 | 287 |  | 1 | 4.7833 | 35 | 0.13667 | 0.68333
Coral Power |  | x |  | 5 | 91 | 10 | 300 | 0 | 0 | 391 |  | 1 | 6.5167 | 35 | 0.18619 | 0.93095
CPE - CenterPoint Energy | x |  |  | 330 | 6807 |  |  |  |  | 6807 |  | 1 | 113.45 | 35 | 3.2414 | 16.2071
CPS - City Public Services | x |  |  | 84 | 1759 |  |  |  |  | 1759 |  | 1 | 29.3167 | 35 | 0.83762 | 4.1881
|  | x |  | 7 | 513 | 26 | 780 | 0 | 0 | 1293 |  | 1 | 21.55 | 35 | 0.61571 | 3.0786
Denton Municipal Electric | x |  |  | 10 | 174 |  |  |  |  | 174 |  | 1 | 2.9 | 35 | 0.082857 | 0.41429
Dynergy |  | x |  | 1 | 87 | 7 | 210 | 0 | 0 | 297 |  | 1 | 4.95 | 35 | 0.14143 | 0.70714
Exelon |  | x |  | 4 | 478 | 32 | 960 | 15 | 450 | 1888 |  | 1 | 31.4667 | 35 | 0.89905 | 4.4952
FPL |  | x |  | 11 | 341 | 23 | 690 | 0 | 0 | 1031 |  | 1 | 17.1833 | 35 | 0.49095 | 2.4548
Garland Power and Light | x |  |  | 23 | 492 |  |  |  |  | 492 |  | 1 | 8.2 | 35 | 0.23429 | 1.1714
|  | x |  | 3 | 156 | 7 | 210 | 2 | 60 | 426 |  | 1 | 7.1 | 35 | 0.20286 | 1.0143
GEUS - Greenville | x |  |  | 7 | 43 |  |  |  |  | 43 |  | 1 | 0.71667 | 35 | 0.020476 | 0.10238
LCRA - Lower Colorado River | x |  |  | 278 | 6336 |  |  |  |  | 6336 |  | 1 | 105.6 | 35 | 3.0171 | 15.0857
|  | x |  | 13 | 697 | 25 | 750 | 3 | 90 | 1537 |  | 1 | 25.6167 | 35 | 0.7319 | 3.6595
Mirant Energy |  | x |  | 1 | 105 | 4 | 120 | 0 | 0 | 225 |  | 1 | 3.75 | 35 | 0.10714 | 0.53571
NRG |  | x |  | 8 | 1151 | 47 | 1410 | 7 | 210 | 2771 |  | 1 | 46.1833 | 35 | 1.3195 | 6.5976
OXY - Occidental Power Svcs |  | x |  | 2 | 162 | 7 | 210 | 8 | 240 | 612 |  | 1 | 10.2 | 35 | 0.29143 | 1.4571
PUB - Brownsville Public Utilities | x |  |  | 15 | 268 |  |  |  |  | 268 |  | 1 | 4.4667 | 35 | 0.12762 | 0.6381
Reliant |  | x |  | 10 | 341 | 52 | 1560 | 21 | 630 | 2531 |  | 1 | 42.1833 | 35 | 1.2052 | 6.0262
RCEC - Rayburn County Electric | x |  |  | 21 | 126 |  |  |  |  | 126 |  | 1 | 2.1 | 35 | 0.06 | 0.3
STEC - South Texas Electric Coop | x |  |  | 143 | 1983 |  |  |  |  | 1983 |  | 1 | 33.05 | 35 | 0.94429 | 4.7214
|  | x |  | 5 | 381 | 16 | 480 | 2 | 60 | 921 |  | 1 | 15.35 | 35 | 0.43857 | 2.1929
Suez Energy Marketing |  | x |  | 2 | 65 | 5 | 150 | 1 | 30 | 245 |  | 1 | 4.0833 | 35 | 0.11667 | 0.58333
Tenaska Power Services |  | x |  | 14 | 908 | 41 | 1230 | 25 | 750 | 2888 |  | 1 | 48.1333 | 35 | 1.3752 | 6.8762
TMPA - Texas Muni Power Auth | x |  |  | 9 | 368 |  |  |  |  | 368 |  | 1 | 6.1333 | 35 | 0.17524 | 0.87619
TNMP - Texas New Mexico Pow | x |  |  | 134 | 2373 |  |  |  |  | 2373 |  | 1 | 39.55 | 35 | 1.13 | 5.65
TXU - Texas Utilities | x |  |  | 1233 | 26641 |  |  |  |  | 26641 |  | 1 | 444.0167 | 35 | 12.6862 | 63.431
|  | x |  | 29 | 2549 | 59 | 1770 | 17 | 510 | 4829 |  | 1 | 80.4833 | 35 | 2.2995 | 11.4976
TOTAL |  |  | 0 | 3540 | 76617 | 530 | 15900 | 139 | 4170 | 96687 |  |  | 1611.45 |  | 46.0414 | 230.2071

## P2P Schedule
MP | Nodal Points | Days | Hours | M a y | [17 empty] | J u n e | [29 empty] | J u l y | [30 empty] | A u g u s t | [30 empty] | S e p t e m b e r
|  |  |  | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30 | 31 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20 | 21 | 22 | 23 | 24 | 25 | 26 | 27 | 28 | 29 | 30
QSE List |  |  |  | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S | M | T | W | T | F | S | S
AEN - Austin Energy | 1322 | 3.1476 | 22.0333 | bar: J u l y 23 M to J u l y 25 W
AEP - American Electric Power | 694 | 1.6524 | 11.5667
APX | 3192 | 7.6 | 53.2 | bar: J u l y 9 M to J u l y 13 F; J u l y 16 M to J u l y 18 W
BEC - Brazos Electric Coop | 757 | 1.8024 | 12.6167 | bar: J u l y 26 T to J u l y 27 F
BTU - Bryan Texas Utilities | 1165 | 2.7738 | 19.4167 | bar: J u l y 23 M to J u l y 25 W
Calpine Power Management | 2561 | 6.0976 | 42.6833 | bar: J u l y 9 M to J u l y 13 F; J u l y 16 M
Constellation Energy | 287 | 0.68333 | 4.7833 | bar: J u l y 20 F
Coral Power | 391 | 0.93095 | 6.5167 | bar: J u l y 19 T
CPS - City Public Services | 1293 | 3.0786 | 21.55 | bar: J u l y 23 M to J u l y 26 T
Dynergy | 297 | 0.70714 | 4.95
Exelon | 1888 | 4.4952 | 31.4667 | bar: J u l y 9 M to J u l y 13 F
FPL | 1031 | 2.4548 | 17.1833 | bar: J u l y 18 W to J u l y 20 F
Garland Power and Light | 426 | 1.0143 | 7.1 | bar: J u l y 23 M
LCRA - Lower Colorado River | 1537 | 3.6595 | 25.6167 | bar: J u l y 17 T to J u l y 20 F
Mirant Energy | 225 | 0.53571 | 3.75 | bar: J u l y 24 T
NRG | 2771 | 6.5976 | 46.1833 | bar: J u n e 25 M to J u n e 29 F; J u l y 2 M
OXY - Occidental Power Svcs | 612 | 1.4571 | 10.2 | bar: J u l y 25 W to J u l y 26 T
Reliant | 2531 | 6.0262 | 42.1833 | bar: J u l y 3 T to J u l y 6 F
STEC - South Texas Electric Coop | 921 | 2.1929 | 15.35 | bar: J u l y 18 W to J u l y 20 F
Suez Energy Marketing | 245 | 0.58333 | 4.0833 | bar: J u l y 27 F
Tenaska Power Services | 2888 | 6.8762 | 48.1333 | bar: J u l y 9 M to J u l y 13 F; J u l y 16 M to J u l y 17 T
TXU - Texas Utilities | 4829 | 11.4976 | 80.4833 | bar: J u l y 30 M to A u g u s t 3 F; A u g u s t 6 M to A u g u s t 10 F; A u g u s t 13 M
TSP List
AEN - Austin Energy | 2042 | 4.8619 | 34.0333 | bar: A u g u s t 6 M to A u g u s t 10 F
AEP - American Electric Power | 10932 | 26.0286 | 182.2 | bar: J u l y 30 M to A u g u s t 3 F; A u g u s t 6 M to A u g u s t 10 F; A u g u s t 13 M to A u g u s t 17 F; A u g u s t 20 M to A u g u s t 24 F; A u g u s t 27 M to A u g u s t 31 F
BEC - Brazos Electric Coop | 4169 | 9.9262 | 69.4833 | bar: J u l y 30 M to A u g u s t 3 F; A u g u s t 6 M to A u g u s t 10 F
BTU - Bryan Texas Utilities | 311 | 0.74048 | 5.1833 | bar: J u l y 27 F
CPE - CenterPoint Energy | 6807 | 16.2071 | 113.45 | bar: J u n e 1 F; J u n e 4 M to J u n e 8 F; J u n e 11 M to J u n e 15 F; J u n e 18 M to J u n e 22 F
CPS - City Public Services | 1759 | 4.1881 | 29.3167 | bar: A u g u s t 14 T to A u g u s t 17 F
Denton Municipal Electric | 174 | 0.41429 | 2.9 | bar: S e p t e m b e r 3 M
Garland Power and Light | 492 | 1.1714 | 8.2 | bar: J u l y 27 F
GEUS - Greenville | 43 | 0.10238 | 0.71667 | bar: S e p t e m b e r 4 T
LCRA - Lower Colorado River | 6336 | 15.0857 | 105.6 | bar: A u g u s t 13 M to A u g u s t 17 F; A u g u s t 20 M to A u g u s t 24 F; A u g u s t 27 M to A u g u s t 31 F
PUB - Brownsville Public Utilities | 268 | 0.6381 | 4.4667 | bar: S e p t e m b e r 5 W
RCEC - Rayburn County Electric | 126 | 0.3 | 2.1 | bar: S e p t e m b e r 6 T
STEC - South Texas Electric Coop | 1983 | 4.7214 | 33.05 | bar: A u g u s t 20 M to A u g u s t 24 F
TMPA - Texas Muni Power Auth | 368 | 0.87619 | 6.1333 | bar: S e p t e m b e r 7 F
TNMP - Texas New Mexico Pow | 2373 | 5.65 | 39.55 | bar: A u g u s t 27 M to A u g u s t 31 F
TXU - Texas Utilities (stream 1) | 8880.3333 | 21.1437 | 148.0056 | bar: J u n e 11 M to J u n e 15 F; J u n e 18 M to J u n e 22 F; J u n e 25 M to J u n e 29 F; J u l y 2 M to J u l y 6 F
TXU - Texas Utilities (stream 2) | 8880.3333 | 21.1437 | 148.0056 | bar: J u n e 11 M to J u n e 15 F; J u n e 18 M to J u n e 22 F; J u n e 25 M to J u n e 29 F; J u l y 2 M to J u l y 6 F
TXU - Texas Utilities (stream 3) | 8880.3333 | 21.1437 | 148.0056 | bar: J u n e 11 M to J u n e 15 F; J u n e 18 M to J u n e 22 F; J u n e 25 M to J u n e 29 F; J u l y 2 M to J u l y 6 F

## P2P Results
MP | TSP | QSE | Metrics | # of Points Checked | # of Points to Check | % of Total Points | % of Points Checked | ERCOT Error Detail | Missing Equipment on Network Model | Missing Points | Mis-Mapped Points | Quality Code Issue - Field Telemeted | Quality Code Issue - Not Field Telemeted | Polarity Reversed | Point not Directly Routed to ERCOT | ERCOT Error SUMMARY | ERCOT # of Errors Found | % of ERCOT Non-Quality Code Errors | TOTAL % of ERCOT Errors
AEN - Austin Energy | x |  |  | 0 | 2042 | 2.112% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 1322 | 1.367% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
AEP - American Electric Power | x |  |  | 0 | 10932 | 11.31% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 694 | 0.7178% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
APX |  | x |  | 0 | 3192 | 3.301% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
BEC - Brazos Electric Coop | x |  |  | 0 | 4169 | 4.312% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 757 | 0.7829% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
BTU - Bryan Texas Utilities | x |  |  | 0 | 311 | 0.3217% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 1165 | 1.205% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Calpine Power Management |  | x |  | 0 | 2561 | 2.649% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Constellation Energy |  | x |  | 0 | 287 | 0.2968% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Coral Power |  | x |  | 0 | 391 | 0.4044% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
CPE - CenterPoint Energy | x |  |  | 0 | 6807 | 7.04% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
CPS - City Public Services | x |  |  | 0 | 1759 | 1.819% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
| x | x |  | 0 | 1293 | 1.337% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Denton Municipal Electric | x |  |  | 0 | 174 | 0.18% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Dynergy |  | x |  | 0 | 297 | 0.3072% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Exelon |  | x |  | 0 | 1888 | 1.953% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
FPL |  | x |  | 0 | 1031 | 1.066% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Garland Power and Light | x |  |  | 0 | 492 | 0.5089% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 426 | 0.4406% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
GEUS - Greenville | x |  |  | 0 | 43 | 0.04447% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
LCRA - Lower Colorado River | x |  |  | 0 | 6336 | 6.553% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 1537 | 1.59% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Mirant Energy |  | x |  | 0 | 225 | 0.2327% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
NRG |  | x |  | 0 | 2771 | 2.866% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
OXY - Occidental Power Svcs |  | x |  | 0 | 612 | 0.633% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
PUB - Brownsville Public Utilities | x |  |  | 0 | 268 | 0.2772% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Reliant |  | x |  | 0 | 2531 | 2.618% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
RCEC - Rayburn County Electric | x |  |  | 0 | 126 | 0.1303% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
STEC - South Texas Electric Coop | x |  |  | 0 | 1983 | 2.051% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 921 | 0.9526% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Suez Energy Marketing |  | x |  | 0 | 245 | 0.2534% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
Tenaska Power Services |  | x |  | 0 | 2888 | 2.987% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TMPA - Texas Muni Power Auth | x |  |  | 0 | 368 | 0.3806% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TNMP - Texas New Mexico Pow | x |  |  | 0 | 2373 | 2.454% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TXU - Texas Utilities | x |  |  | 0 | 26641 | 27.55% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
|  | x |  | 0 | 4829 | 4.994% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%
TOTAL |  |  | 0 | 0 | 96687 | 100% | 0% |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0% | 0%