| OGRR Number | 196 | OGRR Title | Conformance with PRR705, Emergency Interruptible Load Service (EILS) |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision (include Section No. and Title) |  | 4.5, Emergency Electric Curtailment Plan (EECP) 4.5.3.3, EECP Steps |  |
| Protocol Section Requiring Revision, if any. |  |  |  |
| Requested Resolution (Normal or Urgent) |  | ## Urgent |  |
| Revision Description |  | This Operating Guide Revision Request (OGRR) conforms the Operating Guides with PRR705 to allow for the use of Emergency Interruptible Load Service (EILS) when an Emergency Electric Curtailment Plan (EECP) is declared and all available generation and Loads acting as Resources (LaaRs) have been deployed. |  |
| ###### Reason for Revision |  | To conform the Operating Guides with PRR705 language approved by the ERCOT Board on April 18, 2007. |  |
| Timeline |  |  |  |
| Date Posted |  | May 1, 2007 |  |
| Please access the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Paul Wattles |
| E-mail Address | pwattles@ercot.com |
| Company | ERCOT |
| Company Address | 2705 West Lake Dr., Taylor, TX 76574 |
| Phone Number | 512-248-6578 |
| Fax Number | 512-248-6560 |

ERCOT/Market Segment Impacts and Benefits

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | None. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Conform with Protocol language and PUC Substantive Rules. | None. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | PRR 705, ERCOT Emergency Interruptible Load Service (EILS), which was approved by the ERCOT Board on April 18, 2007, conforms the ERCOT Protocols with PUCT Substantive Rule § 25.507. The only impact of PRR 705 on the Operating Guides is the revision to the Emergency Electric Curtailment Plan (EECP). This OGRR will conform the Guides to the revised Protocols. |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other | 1 |  |  |
| Comments | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

Proposed Operating Guide Language Revision

## 4.5	Emergency Electric Curtailment Plan (EECP)

Reference:  Protocol Section 5.6.6.1, Emergency Electric Curtailment Plan (EECP)

At times it may be necessary to reduce electrical demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing demand during such emergencies, ERCOT will initiate and coordinate the implementation of the Emergency Electric Curtailment Plan following the EECP Steps set forth below in Section 5.6.7, EECP Steps.

The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.

ERCOT’s operating procedures shall meet the following goals while continuing to respect the confidentiality of market sensitive data:

- Use of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT system;

- Use of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

- Maximum use of ERCOT System capability;

- Maintenance of station service for nuclear Generation Resource Facilities;

- Securing of startup power for Generation Resources;

- Operation of power Generation Resources during loss of communication with ERCOT;

- Restoration of service to critical Loads in the manner defined in the Operating Guides; and

(8) 	Restoration of service to all customers following major system disturbances, giving priority to the larger groups of customers.

ERCOT shall be responsible for coordinating with QSEs and TDSPs to monitor system conditions, initiating the EECP steps, notifying all QSEs, and coordinating the implementation of the EECP Steps while maintaining transmission security limits.

ERCOT, at management’s discretion, may at any time issue an appeal through the public news media for voluntary energy conservation.

During the EECP, ERCOT has the authority to obtain energy from BtB Ties or Block Load Transfers (BLTs) from non-ERCOT Control Areas when capacity is available.

Some of the EECP Steps will not be applicable if transmission security violations exist. There may be insufficient time to implement all Steps in sequence, but to the extent practicable, ERCOT will use Ancillary Services which bidders have made available in the market to maintain or restore reliability.

ERCOT may immediately implement Step 3 of the EECP any time the steady-state system frequency is below 59.8 Hz and will immediately implement Step 3 any time the steady-state frequency is below 59.5 Hz.

Percentages for Step 3 Load shedding will be based on previous year’s TDSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

Reference:  Protocol Section 5.6.7, EECP Steps

Step 1 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal to 2300 MW.

ERCOT will:

(1)	Utilize available DC tie capability that is not already being used by the market;

(2)	Notify the Southwest Power Pool Security Coordinator; and

(3)	Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency.

(4)		Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers.

QSEs will:

(1)  	Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency.

Step 2 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW Provided from LaaR Equal to 1750 MW.

In addition to measures associated with Step 1, ERCOT will:

(1)	Instruct TDSPs to reduce Customers load by using distribution voltage reduction measures, if deemed beneficial by the TDSP;

(2)	Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (controlled by high-set under-frequency relays);

(3)	With the approval of the affected Non-ERCOT control area, may instruct TDSPs to implement BLTs, which transfer load from the ERCOT control area to Non-ERCOT control areas.  Use of a BLT will be defined in the ERCOT Operating Guides; and

(4)	Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation.

Step 3 – Maintain system frequency at 60 Hz:

Following deployment of the measures associated with Steps 1 and 2, ERCOT will deploy all available EILS Resources as a single block via a single Verbal Dispatch Instruction to all QSEs providing EILS.

Step 4 — Maintain system frequency at 59.8 Hz or greater

In addition to measures associated with Steps 1, 2 and 3, ERCOT will direct all TDSPs and their agents to shed firm Load, in one hundred (100) megawatt (MW) blocks, distributed as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hertz (Hz).  ERCOT may take this action prior to the expiration of the ten (10) minute EILS Resource deployment period if ERCOT, in its sole discretion, believes that shedding firm Load is necessary to maintain the stability of the ERCOT System.  If, due to ERCOT System conditions, EILS Resources are not deployed prior to this action, ERCOT shall deploy EILS Resources as soon as possible following this action.

In addition to measures associated with Steps 1 and 2, TDSPs will keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens.  Whenever possible, TDSPs shall not manually drop Load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan.

Reference:  Protocol Section 5.6.7.1, Restoration of Market Operations

ERCOT shall continue EECP until sufficient bids are received and deployed by ERCOT to eliminate the conditions requiring the EECP.  ERCOT shall release EILS Resources after both the restoration of RRS capacity and initiation of the restoration of Loads acting as Resources.

Reference:  Protocol Section 6.1.13, Emergency Interruptible Load Service (EILS)

Consistent with subsection (a) of PUCT Subst. Rule § 25.507, Electric Reliability Council of Texas (ERCOT) Emergency Interruptible Load Service (EILS) is defined as a special emergency service used during an EECP Step 3 or 4 to reduce Load and assist in maintaining or restoring ERCOT System frequency.

As provided by ERCOT to QSEs:  A special emergency service used by ERCOT in EECP Step 3 prior to ERCOT instructing TDSPs to shed firm Load, or in EECP Step 4 if deployment in Step 3 was not possible.

As provided by a QSE to ERCOT:  The provision of capacity by Load Resources capable of reducing their electricity consumption during Step 3 or Step 4 of EECP.

#### 4.5.3.3	EECP Steps

Step 1 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal To 2300 Mw

| OPERATOR | ACTION |
| --- | --- |
| ERCOT | - Utilize available DC tie capability that is not already being used by the market. - Notify the Southwest Power Pool Security Coordinator. - Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency. - Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers. |
| QSE | - Notify ERCOT of any resources uncommitted but available in the timeframe of the emergency. |

Step 2 – Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW Provided from LaaR Equal To 1750 MW

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures associated with STEP 1 |
| ERCOT | - Instruct TDSPs to reduce customer loads by using distribution voltage reduction measures, if deemed beneficial by the TDSP. - Instruct QSEs to deploy all Responsive Reserve, which is supplied from Load acting as a Resource (LaaRs) (controlled by high-set under-frequency relays) - With approval of the affected Non-ERCOT control area, may instruct TDSPs to implement Block Load Transfer, which transfer load from the ERCOT control area to Non-ERCOT control areas. - Unless such a media appeal is already in effect, ERCOT staff shall issue an appeal through the public news media for voluntary energy conservation. |

Step 3 - Maintain System Frequency At 60 Hz

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1 and 2. |
| ERCOT | Deploy all available EILS Resources as a single block via a single Verbal Dispatch Instruction to all QSEs providing EILS. |

Step 4 - Maintain System Frequency At 59.8 Hz Or Greater

| OPERATOR | ACTION |
| --- | --- |
|  | In addition to measures under STEPS 1, 2, and 3. |
| ERCOT | Direct all TDSPs and their agents to shed firm Load, in one hundred (100) megawatt (MW) blocks, distributed as agreed and documented in the ERCOT Operation procedures in order to maintain a steady state system frequency of 59.8 Hertz (Hz). ERCOT may take this action prior to the expiration of the ten (10) minute EILS Resource deployment period if ERCOT, in its sole discretion, believes that shedding firm Load is necessary to maintain the stability of the ERCOT System. If, due to ERCOT System conditions, EILS Resources are not deployed prior to this action, ERCOT shall deploy EILS Resources as soon as possible following this action. |
|  | In addition to measures under STEPS 1 and 2. |
| TDSPs | Keep in mind the need to protect the safety and health of the community and the essential human needs of the citizens. Whenever possible, TDSPs shall not manually drop Load connected to under-frequency relays during the implementation of the Emergency Electric Curtailment Plan. |

Obligation for load shed is by DSP.  Load shedding obligations need to be represented by an entity with 7x24 operations and hotline communications with ERCOT and control over breakers.  [Use Transmission Operators (TOs) as list of entities.]

ERCOT Load Shed Table

| Transmission Operator | 2005 Total Transmission Operator Load (MW) |
| --- | --- |
| American Electric Power | 9.50 |
| Austin Energy | 3.90 |
| Brazos Electric Power Cooperative | 3.89 |
| CenterPoint Energy | 24.56 |
| City of Bryan | 0.53 |
| City of College Station | 0.29 |
| City of Denton | 0.50 |
| City of Garland | 0.99 |
| City Public Service of San Antonio | 7.05 |
| Lower Colorado River Authority | 4.96 |
| Magic Valley Electric Cooperative | 0.53 |
| Public Utility Board of Brownsville | 0.41 |
| Rayburn Country Electric Cooperative | 1.00 |
| South Texas Electric Coop-Medina Electric Coop | 0.60 |
| Texas New Mexico Power | 2.26 |
| Tex-La | 0.15 |
| TXU-Electric Delivery | 38.88 |
| ERCOT Total | 100.00 |