# ERCOT Operations Report for ROS & OWG

# April 2007

## Frequency Control

| Frequency Control (<59.9 HZ or >60.1 Hz) |  |  |  |
| --- | --- | --- | --- |
| Time | Freq (Hz) | Duration (mm:ss) |  |
| 04/04 07:54 | 59.867 | :06 | 550 MW resource lost |
| 04/10 09:13 | 59.899 | :02 | 380 MW lost on 3 resource train |
| 04/12 07:56 | 59.81 | :58 | 720 MW lost on 4 resource train |
| 04/15 00:25 | 60.105 | :18 | 1740 MW schedule change across midnight, ERCOT load of 26000 and dropping, 250 MW ncl change. |
| 04/19 17:59 | 60.165 | 9:04 | Significant negative SCE over previous intervals corrected and Down Regulation was depleted |
| 04/24 06:00 | 60.103 | :10 | 3650 schedule change. Significant positive SCE by one QSE. |
| 04/25 02:33 | 59.897 | :04 | 260 MW resource lost. Unit output dropped from 560 MW over previous hours prior to trip. Frequency at 59.96 at time of trip. Large negative ERCOT SCE. |
| 04/29 13:43 | 59.899 | :06 | Runback and trip of 500 MW on 3 resource train |

Deployed Responsive (14) (Reported Above)

|  | Deployed | Duration | Max Deployed | Details |
| --- | --- | --- | --- | --- |
|  |  | (h:mm:ss) | (MW) |  |
| 1 | 4/2 8:06 | 0:07:24 | 253.76 | QSEs not following schedule |
| 2 | 4/4 0:01 | 0:07:10 | 278.73 | QSEs not following schedule |
| 3 | 4/4 7:54 | 0:22:16 | 428.48 | Unit Trip |
| 4 | 4/6 8:57 | 0:09:46 | 262.08 | Unit Trip |
| 5 | 4/10 9:13 | 0:05:58 | 295.37 | Unit Trip |
| 6 | 4/12 7:56 | 0:09:24 | 665.6 | Unit Trip |
| 7 | 4/19 23:53 | 0:11:52 | 262.08 | QSEs not following schedule |
| 8 | 4/23 22:02 | 0:08:20 | 266.25 | QSEs not following schedule |
| 9 | 4/24 23:19 | 0:03:26 | 270.41 | QSEs not following schedule |
| 10 | 4/25 2:33 | 0:10:36 | 303.69 | Unit Trip |
| 11 | 4/27 11:03 | 0:04:56 | 278.73 | QSEs not following schedule |
| 12 | 4/28 1:59 | 0:05:12 | 262.08 | Unit Trip |
| 13 | 4/28 23:58 | 0:10:14 | 278.73 | QSEs not following schedule |
| 14 | 4/29 13:43 | 0:04:00 | 295.37 | Unit Trip |

7/14 of these events are due to unit trip

Day-Ahead RMR and OOMC Capacity Purchases

| Historical Totals | Apr-06 | Mar07 | Apr-07 |
| --- | --- | --- | --- |
| Austin | 18 | 11 | 76 |
| Bryan Area | 61 | 0 | 9 |
| Corpus | 1 | 0 | 2 |
| DFW | 23 | 6 | 18 |
| E RIO | 166 | 7 | 1 |
| Houston | 49 | 7 | 6 |
| Laredo | 66 | 56 | 55 |
| North | 9 | 4 | 0 |
| Northeast | 12 | 4 | 0 |
| San Antonio | 17 | 4 | 20 |
| South | 19 | 8 | 1 |
| W RIO | 194 | 66 | 5 |
| Western | 20 | 22 | 7 |
| Total | 655 | 195 | 200 |

| Data in detail | RMR | OOMC | RPRS | Total |
| --- | --- | --- | --- | --- |
| Austin | 0 | 6 | 70 | 76 |
| Bryan Area | 0 | 0 | 9 | 9 |
| Corpus | 0 | 0 | 2 | 2 |
| DFW | 0 | 18 | 0 | 18 |
| E RIO | 0 | 0 | 1 | 1 |
| Houston | 0 | 0 | 6 | 6 |
| Laredo | 55 | 0 | 0 | 55 |
| North | 0 | 0 | 0 | 0 |
| Northeast | 0 | 0 | 0 | 0 |
| San Antonio | 0 | 10 | 10 | 20 |
| South | 0 | 0 | 1 | 1 |
| W RIO | 0 | 4 | 1 | 5 |
| Western | 0 | 6 | 1 | 7 |
| Total | 55 | 44 | 101 | 200 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

## OOME / Congestion Management Activity:

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Temple Pecan Creek-Tradinghouse/Temple -Lake Creek | Lake Creek-Temple Pecan Creek | 26 |
| Temple Pecan Creek-Tradinghouse/Temple -Lake Creek | Evant - Adamsville 138 kV | 13 |
| Clear Springs & Marion - Zorn 345 kV | Clear Springs Auto 345/138 kV | 10 |
| Gibbons Creek - Twin Oak Switch345 kV | Jewett - Watson Chapel 138 kV | 9 |
| Sonora - Hamilton Rd 138 kV | Fort Lancaster - Illinois #4 69 kV | 8 |
| Lytton Spring - Zorn and Austrop - Zorn 345 kV | Canyon - Rohr 138 kV | 6 |
| Centerville Road Switch - Forney Switch 345 kV | Lake Hubbard-Duck Creek Tap | 5 |
| STP - Skyline and Whitepoint 345kV | Blessing - Lolita 138kV | 5 |
| Clear Springs & Marion - Zorn 345 kV | Seguin - Seguin West 138 kV | 4 |
| Kendall - Hays Energy 345 kV | Seguin - Seguin West 138 kV | 4 |
| Cal Energy - Morgan Creek 345 kV | Midland East - Big Springs West | 3 |
| Centerville Road Switch - Forney Switch 345 kV | Duck Creek Tap - Forney Tap 138 kV | 3 |
| Menard - Gillespie 138 kV | Menard Auto 138/69 kV | 3 |
| Clear Springs - Marion 345 kV | Clear Springs Auto 345/138 kV | 2 |
| Dilley Switch - North Laredo 138 kV | Asherton - North Laredo 138 kV | 2 |
| Farmersville - Monticello SES 345 kV | Allen Switch Auto 345/138 kV | 2 |
| North Edinburg Auto 1 345/138 kV | North Edinburg Auto 2 345/138 kV | 2 |
| Templwe Switch - Killeen Switch & Sandow Switch 345 kV | Killeen Taft Street - Killeen Elm 138 kV | 2 |
| Midland East - Odessa EHV 345 kV | Odessa Switch - Big Three Odessa Tap | 1 |
| Fort Lancaster - Mesa View 138 kV | McCamey - Big Lake 138 kV | 1 |
| Marion - Guadalupe Gen 345 kV | Seguin - Seguin West 138 kV | 1 |
| Comal - Loop 337 138 kV | Seguin - Seguin West 138 kV | 1 |
| Farmersville - Valley 345 kV | Allen Switch Auto 345/138 kV | 1 |
| Farmersville - Monticello SES 345 kV | Monticello - Sulphur Springs 345 kV | 1 |
| Breckenrdige Auto 138/69 kV | Olney POD - Graham 69 kV | 1 |
| Gibbons Creek Auto 345/138 kV | Gibbons Creek - Bryan Greens Prairie | 1 |
| Graham - Parker & Benbrook 345 kV | Willow Creek - Parker 345 kV | 1 |
| Graham - Parker & Benbrook 345 kV | Olney 138/69 kV | 1 |
| Kendall - Cagnon 345 kV | Shertz - Parkway 138 kV | 1 |
| North Edinburg- Rio Hondo 345 kV | South McAllen - Hidalgo 69 kV | 1 |
| Odessa EHV Auto 1 345/138 kV/Morgan Creek - Odessa | Odessa Auto 2 345/138 kV | 1 |
| San Miguel Switchyard - Sigmor 138 kV | Kennedy Switch Kennedy Sub 69 kV | 1 |
| Silas Ray 138/69 kV T1 | Silas Ray 138/69 kV T2 | 1 |
| STP - Whitepoint 345 kV | Blessing - Lolita 138kV | 1 |
| Marion - Zorn 345 kV | Seguin - Seguin West 138 kV | 1 |
| Temple Switch-Tradinghouse/Temple Switch-Lake Creek | Lake Creek - Temple Pecan Creek | 1 |

## Zonal OC1’s

| CSC | Days |
| --- | --- |
| North - Houston | 12 |
| West - North | 5 |
| South - Houston | 1 |

## New RAPs

2007 Remedial Action Plans Finalized on 5/4.

## New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin No. |
| --- | --- | --- |
| 04/26/2007 | Transmission & Security Desk V3.0 Rev 82 | 326 |
| 04/26/2007 | Frequency Control Desk V3.0 Rev 53 | 325 |
| 04/25/2007 | Operating Period Desk V2R20 | 324 |
| 04/03/2007 | Shift Supervisor Desk V3Rev36 | 323 |

## Blackout/Load Shed incidences

None

## EECP

None

## Major system voltage problems

None

## Voltage Instructions

None

## Major Computer Problems, Enhancements & Fixes

4/10	RTCAM trials commenced.

## Communication

4/5	Held intervals 09:30 and 09:45 due to software problems.

4/5	Held intervals 11:15 and 11:30 due to software problems.

## ERCOT peak (Unofficial)

4/3 	17:00	41688

## Yearly Mid-Term Load Forecast Error Comparison

| Yearly Mid-Term (Hourly) Load Forecast Error Comparison |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | MAPE for MTLF run at 16:00 Day Ahead (2004) | MAPE for MTLF run at 16:00 Day Ahead (2005) | MAPE for MTLF run at 16:00 Day Ahead (2006) | MAPE for MTLF run at 16:00 Day Ahead (2007) |
| April | 3.23 | 3.37 | 5.59 | 3.00 |
| Average Annual | 4.08 | 4.56 | 3.79 | 3.50 |

## OCN, Advisory, Alerts, and Emergency Notices

### Generation:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 4/2/07 | 8:06 | 8:13 | Frequency spiked to 59.909Hz. Deployed 253MW of responsive reserve service due to slow response of QSEs and nonconforming loads ramping up. ERCOT load 30673. |
| 4/3/07 | 14:30 | 18:45 | Deployed Non-Spin Reserve Service |
| 4/4/07 | 0:01 | 0:04 | Deployed 279 MW of Responsive Reserve when Frequency dropped to 59.903, Schedule changes, slow unit response and non conforming loads. |
| 4/4/07 | 7:54 | 8:17 | Deployed 400mws of RRS due to XXXX trip of 550mws. Frequency dropped to 59.867, ERCOT load 31,021. |
| 4/6/07 | 8:57 | 9:07 | Frequency spiked to 59.907Hz. XXXX tripped with 404MW, deployed 262MW of responsive reserve service. ERCOT load 28382. |
| 4/10/07 | 9:14 | 9:17 | XXXX tripped with 382 MW. Frequency spiked to 59.899Hz, deployed 295 MW of Responsive Reserve Service. ERCOT load 31022. |
| 4/10/07 | 13:08 | 16:20 | Activated Simultaneous Feasibility Test (SFT) for Real Time Constraint Activity Manager (RTCAM) in the Real-Time Balancing Market for market test trials. |
| 4/11/07 | 12:58 | 16:20 | Activated Simultaneous Feasibility Test (SFT) for Real Time Constraint Activity Manager (RTCAM) in the Real-Time Balancing Market for market test trials. |
| 4/12/07 | 7:56 | 7:59 | XXXX tripped with 723 MW. Frequency spiked to 59.810Hz, deployed 666 MW of Responsive Reserve Service. ERCOT load 29,681. |
| 4/12/07 | 8:40 | 15:52 | Activated Simultaneous Feasibility Test (SFT) for Real Time Constraint Activity Manager (RTCAM) in the Real-Time Balancing Market for market test trials. |
| 4/15/07 | 0:26 | 0:28 | Frequency spiked up to 60.10 Hz due to non conforming loads and SCE errors. |
| 4/19/07 | 23:54 | 0:05 | Frequency spiked to 59.907Hz. Deployed 262MW's of responsive reserve service due to slow response of QSEs, wind dropped and non conforming loads ramping up. ERCOT load 27015mw. |
| 4/23/07 | 22:02 | 22:10 | Deployed 266 mw of Responsive Reserve Service, frequency dropped below 59.91 Hz due to schedule changes and slow unit response. ERCOT load of 34312. |
| 4/24/07 | 23:19 | 23:22 | Deployed 270 mw of Responsive Reserve Service, frequency dropped below 59.91 Hz due to schedule changes and slow unit response. ERCOT load of 29080. |
| 4/25/07 | 2:33 | 2:43 | Frequency spiked to 59.91Hz due to XXXX tripping with 250 MW. Deployed 303 MW of Responsive Reserve Service. ERCOT load 24,433. |
| 4/27/07 | 11:03 | 11:08 | Deployed 278 MW of Responsive Reserve Service, frequency dropped below 59.904 Hz due to schedule changes and slow unit response. ERCOT load of 31692. |
| 4/28/07 | 2:00 | 2:05 | Deployed 262 MW of Responsive Reserve Service, frequency dropped to 59.907 Hz due to a large unit conducting a load rejection test. ERCOT load of 24155. |
| 4/28/07 | 23:58 | 0:08 | Deployed 279 MW' of Responsive Reserve Service, frequency dropped to 59.909 Hz due to schedule changes, slow unit response. ERCOT load of 28400. |
| 4/29/07 | 13:43 | 13:47 | XXXX tripped with 360 MW. Frequency spiked to 59.899 Hz, deployed 295 MW of Responsive Reserve Service. ERCOT load of 35615. |

### Capacity:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 4/1/07 | 0:01 | 0:05 | Advisory issued for Adjusted Responsive Reserve below 3000 MW. |
| 4/2/07 | 13:08 | 22:37 | Advisory issued for Adjusted Responsive Reserve below 3000 MW. |
| 4/3/07 | 9:30 | 21:07 | Advisory issued for Adjusted Responsive Reserve below 3000 MW. |
| 4/5/07 | 7:00 | 8:55 | Advisory issued due to Adjusted Responsive Reserve below 3000 |
| 4/7/07 | 8:02 | 9:56 | OCN for capacity shortage for hours 21:00, 23:00 and 24:00. |
| 4/14/07 | 1:15 | 2:35 | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 4/14/07 | 9:00 | 14:22 | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 4/14/07 | 20:00 | 23:30 | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 4/15/07 | 1:00 | 06:05 | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 4/17/07 | 1:07 | 6:05 | Advisory issued due to Adjusted Responsive Reserve below 3000 mw. |
| 4/19/07 | 17:28 | 22:25 | Advisory Issued for Adjusted Responsive Reserve below 3000mw. |
| 4/22/07 | 0:05 | 1:45 | Advisory issued at 0005 for Adjusted Responsive Reserve below 3000mw. |
| 4/24/07 | 6:48 | 8:02 | Advisory issued for adjusted responsive reserve below 3000 MW. |
| 4/24/07 | 9:49 | 14:34 | Advisory issued for adjusted responsive reserve below 3000 MW. |
| 4/26/07 | 15:28 | 21:00 | Advisory issued due to adjusted responsive reserve below 3000MW. |
| 4/28/07 | 12:40 | 19:08 | Advisory issued for Adjusted Responsive Reserve below 3000 MW. |
| 4/28/07 | 14:40 | 19:08 | Alert issued for Adjusted Responsive Reserve below 2500 MW. |
| 4/29/07 | 15:27 | 18:14 | Advisory issued for Adjusted Responsive Reserve below 3000 MW. |

### Transmission:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 4/1/07 | 0:01 | 17:57 | Transmission alert for the loss of Monticello SES - Farmersville TU 345kV double circuit overloads Monticello SES - Monticello Mining - Monticello Tap 138kV circuits beyond first contingency limits. |
| 4/3/07 | 14:00 | 22:30 | Transmission Alert - Loss of La Palma 138/69 KV Transformer #1 overloads 138/69 KV Transformer #2 121% of 140 MVA rating |
| 4/12/07 | 15:45 | 24:00 | ERCOT Operation Engineering Support calculated a new West - North limit based on Real Time Contingency Analysis. |
| 4/20/07 | 16:00 | 24:00 | West - North Zonal Limit lowered from 700 mw to 550 mw per ERCOT Engineering. |
| 4/24/07 | 9:15 | 21:30 | Transmission alert for the loss of Gibbons Creek - Twin Oaks 345kv overloads Jewett - Watson Chapel 138kV with no market solution. |
| 4/24/07 | 9:15 | 21:30 | Transmission alert for the loss of Gibbons Creek 345/138kv autotransformer 1 and 2 overloads Jewett - Watson Chapel 138kV with no market solution. |

### Weather:

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 4/6/07 | 7:30 | 24:00 | OCN issued for cold weather Sunday and Monday. |
| 4/7/07 | 7:30 | 24:00 | OCN issued for cold weather Sunday and Monday. |
| 4/8/07 | 00:15 | 15:00 | OCN issued for cold weather Sunday and Monday. |

### Other:

4/2	20:30  Resource trips at 5 plants totaling 151 MW tripped within minutes of each other.  Storms and lightning reported in the area.

4/25 	01:30 – 20:15	Eagle Pass BLT from ERCOT  to CFE to assist recovery from storm damage on the  CFE system .

4/28	01:00 – 04:30	Presidio BLT from ERCOT to CFE to repair switch at Alamito Creek.