Texas Nodal Market

ERCOT Nodal ICCP Communication Handbook

Version 0.11

May 2, 2007

Table of Contents

1.	Introduction	7

1.1	User Prerequisites	7

1.2	Handbook Organization	7

1.3	Conventions Used in this Handbook	8

1.4	References	9

1.5	Glossary	9

2.	Connecting to the ERCOT Wide Area Network	11

2.1	Network Topology Overview	11

2.2	Market Participant Site WAN Connections	12

2.3	Equipment and Services Provided by ERCOT	13

2.3.1	Frame Relay Wide Area Network	14

2.3.2	Point-to-Point DACS Network	14

2.4	High Availability Data Connections	14

2.5	Network Security	15

3.	ICCP Conventions	17

3.1	ICCP Connections	17

3.1.1	Establishing ICCP Associations	17

3.1.2	Association Restrictions (Peer Communication)	19

3.1.3	Association Identifiers	19

3.1.4	Protocol Selectors	20

3.1.5	TCP Port Number	20

3.1.6	System Connections	20

3.2	The ICCP Protocol	21

3.2.1	Supported Features	22

3.2.2	ICCP Version	22

3.2.3	Bilateral Tables	22

3.2.3.1	Bilateral Table Names	22

3.2.3.2	Bilateral Table Version Management	23

3.2.4	ICCP Conformance Blocks	24

3.2.5	ERCOT MMS PDU Size	24

3.3	ICCP Data Exchange Conventions	25

3.3.1	Domain Naming Conventions	25

3.3.2	Data Set Naming Conventions	27

3.3.3	ICCP Object Naming Conventions for Data Available to All Market Participants	28

3.4	Data Quality	31

3.4.1	Quality Codes Illustrated	35

3.4.2	Detail Quality Code Definitions	38

3.4.2.1	ICCP Quality Codes from Market Participants to ERCOT	38

3.4.2.2	ICCP Quality Codes from ERCOT to Market Participants	41

3.5	Data Semantics	45

3.5.1	Status Indication Semantic Conventions	45

3.5.2	Energy and Reactance Value Semantic Conventions	45

3.5.3	Sign Conventions	45

4.	QSE Connection Requirements	47

4.1	QSE Communication Requirements	47

4.2	QSE Implementation Procedures	48

4.3	QSE Association Information Exchange Form (AIEF)	49

4.4	QSE ICCP Data Exchange Requirements	58

4.4.1	QSE ICCP Object Naming Convention	58

4.4.1.1	Object Names for Generation and Regulation	58

4.4.1.2	ICCP Object Names for Non-generation Data	63

4.4.2	QSE Transfer Set Definition Standards	65

4.4.2.1	QSE Requirements for Generation Data	66

4.4.2.2	QSE Requirements for Non-Generation Data	66

4.4.3	Data Sent to QSEs	67

4.4.4	Data Received from QSEs	67

5.	TSP Connection Requirements	71

5.1	TSP Communication Requirements	71

5.2	TSP Implementation Procedures	72

5.3	TSP Association Information Exchange Form (AIEF)	73

5.4	TSP ICCP Data Exchange Requirements	82

5.4.1	ERCOT TSP ICCP Object Naming Convention	82

5.4.2	TSP Transfer Set Definition Standards	82

5.4.3	Data Received from TSPs	82

5.4.4	Optional TSP Data Exchange	82

6.	Data Available to All Market Participants	82

7.	Data Calculated Locally by ERCOT	82

Attachment A ERCOT WAN Connection Agreement	82

Attachment B Market Participant WAN Circuit Installation Site Survey	82

Attachment C Market Participant WAN Equipment Installation Site Survey	82

Attachment D ERCOT WAN Requirement Pricing Survey	82

Index	82

List of Tables:

Table 1 AP Title Format	19

Table 2 Required ICCP Supported Features	22

Table 3 ICCP Object Names for Data Available to All Market Participants	29

Table 4 ERCOT's Determination of a REPLACED Value when Current Provider is Market Participant	32

Table 5 ERCOT's Determination of a REPLACED Value when Current Provider is ERCOT	32

Table 6 ERCOT SCADA Quality Code and ICCP Validity Code Translation to SCADA Quality Codes	33

Table 7 ICCP Attributes for Telemetered Points from Market Participants to ERCOT	38

Table 8 ICCP Attributes for Calculated Points from Market Participants to ERCOT	39

Table 9 ICCP Attributes for Manually Entered Points from Market Participants to ERCOT	39

Table 10 ICCP Attributes for State Estimated Points from Market Participants to ERCOT	40

Table 11 ICCP Attributes for Telemetered Points from ERCOT to Market Participants	41

Table 12 ICCP Attributes for Calculated Points from ERCOT to Market Participants	42

Table 13 ICCP Attributes for Manually Entered Points from ERCOT to Market Participants	43

Table 14 ICCP Attributes for State Estimated Points from ERCOT to Market Participants	43

Table 15 Status Indication Semantic Conventions	45

Table 16 Energy and Reactance Semantic Conventions	45

Table 17 ERCOT ICCP Data Sign Conventions	45

Table 18 QSE Network-wide Information Form	52

Table 19 QSE Primary Site ICCP Node Form	53

Table 20 QSE Secondary Site ICCP Node Information	55

Table 21 QSE Alternate Site ICCP Node Information	57

Table 22 ICCP Object Names for Generation and Regulation Data Sent to QSEs	59

Table 23 ICCP Object Names for Generation Data Received from QSEs	60

Table 24 ERCOT QSE Non-generation ICCP Data Object Naming Conventions	64

Table 25 QSE Generation Transfer Set Requirements	66

Table 26 - Per-QSE Data Sent to QSE	67

Table 27 - Per- Resource Data Sent to QSE	67

Table 28 - Per-Hub Data Sent to QSE	67

Table 29 - Per-Load Zone Data Sent to QSE	67

Table 30 - Per-QSE Data Received from QSE	67

Table 31 - Per-Plant Data Received from QSE	68

Table 32 - Per-Generation Resource Data Received from QSE	68

Table 33 - Per-Load Resource Data Received from QSE	69

Table 34 - Per Wind Resource Data Received from QSE	70

Table 35 TSP Network-wide Information Form	76

Table 36 TSP Taylor Site ICCP Node Form	77

Table 37 TSP Austin Site ICCP Node Information	79

Table 38 TSP Test ICCP Node Information	81

Table 39 ERCOT TSP ICCP Data Object Naming Conventions	82

Table 40 - Per-Buss Data Received from TSP	82

Table 41 - Per-Transformer Data Received from TSP	82

Table 42 - Per-Transmission Line Data Received from TSP	82

Table 43 - Per-Reactor (Inductive or Capacitive) Data Received from TSP	82

Table 44 - Per-Circuit Breaker Data Received from TSP	82

Table 45 - Per-Load Data Received from TSP	82

Table 46 - Per-DC Injection Point Data Received from TSP	82

Table 47 - Per- Block Load Transfer Point Data Received from TSP	82

Table 48 - Per Weather Zone Tie Line Data Received from TSP	82

Table 49 - Per Dynamic Rating Data Received from TSP	82

Table 50 - Data Available for Reading by All Market Participants	82

Table 51 - Per-Transformer Data	82

Table 52 - Per-Transmission Line Data	82

Table 53 - Per-Reactor (Inductive or Capacitive) Data	82

List of Figures

Figure 1 ERCOT Wide Area Network Overview	12

Figure 2 Market Participant Site Diagram	13

Figure 3 High Availability Data Connections	15

Figure 4 ICCP Network Protocol Suite	17

Figure 5 Types of ICCP Associations	18

Figure 6 Single-use Association (ERCOT Server)	19

Figure 7 Single-use Association (Market Participant Server)	19

Figure 8 Domain Names and Their Implementation	27

# Introduction

The ERCOT Nodal ICCP Communication Handbook sets standards, conventions, and fundamental parameters required for Market Participants to exchange data with ERCOT using the ICCP protocol in the Texas Nodal Market. Also included in the Handbook is a description of the physical network infrastructure ERCOT has implemented to facilitate connections between ERCOT facilities and those of the Market Participants.

The Handbook specifies important configuration and functional requirements for ICCP implementations so that the Market Participant’s system will interoperate with ERCOT’s system. Market Participants and, if applicable, their vendors will need this information to include the required features and to build the proper delivered ICCP configuration. Such information includes addressing specifications, naming conventions, required ICCP Conformance Blocks, and required features of the specified Conformance Blocks. Standards are also specified for the interpretation of data values exchanged, and well as quality code semantics.

The Handbook also includes standards for units of measure, value semantics, sign conventions and data object naming conventions. This information is needed by Market Participants in order to exchange the correct values between the Market Participants’ EMS/SCADA systems and the ICCP subsystem.

The ERCOT Nodal ICCP Communication Handbook addresses the connection standards and requirements for ICCP only. Other connections such as the Web Portal, application interfaces, and operating standards are discussed in other documents such as the Texas Nodal Protocols, Texas Nodal Enterprise Integration External Interfaces Specification, and the Texas Nodal Market Operating Guides.

## User Prerequisites

Anyone using this document should have:

- A general knowledge of data communications concepts

- A working knowledge of Energy Management System functions and concepts

- Familiarity with modern data communications technology

- Knowledge of ICCP concepts

- Knowledge of the TCP/IP protocol concepts

- General knowledge of the International Standards Organization’s Open System Interconnection model.

Additionally, Market Participants should be familiar with the ERCOT Network and have a general knowledge of their local EMS/SCADA System.

## Handbook Organization

This ERCOT Nodal ICCP Communication Handbook has been organized to aid the reader in finding essential information easily. The Handbook groups the material into the following three general topics:

- Equipment, equipment interconnections, and physical layer protocols necessary to physically connect a Market Participant’s systems to ERCOT’s systems,

- ICCP parameters, standards, and conventions required for every Market Participant to successfully communicate with ERCOT,

- Procedures, ICCP parameters, and data exchange requirements for each type of Market Participant (QSE or TSP) to reliably exchange operational data with ERCOT on a day to day basis.

Section 1, Introduction describes the purpose and scope of the ERCOT Nodal ICCP Communication Handbook. It includes:

- What the reader should know in order to get the most out of the Handbook (User Prerequisites),

- This section covering the Handbook organization (Handbook Organization),

- Typographical conventions used for describing parameters, constants, and other components of the presentation (Conventions Used in this Handbook),

- References to other documents useful and/or necessary for complete treatment of the Handbook subject matter (References),

- Definitions of terms specific to the scope of the Handbook and not found in the Texas Nodal Protocols (Glossary).

Section 2, Connecting to the ERCOT Wide Area Network presents an overview of the ERCOT WAN and illustrates in detail the ERCOT-provided equipment and connection architecture implemented at each Market Participant’s site(s).

Section 3, ICCP Conventions provides details on the ICCP client/server architecture and describes parameters necessary for all Market Participants to successfully establish communication with ERCOT using ICCP. Included in this section are Association identifiers, ICCP Object naming conventions, units of measure, sign conventions, and state semantics for status indication points.

Section 4, QSE Connection Requirements is dedicated to QSEs and Section 5, TSP Connection Requirements is dedicated to TSPs. These sections are organized in the same manner. Each section describes how a Market Participant initiates the implementation of a connection, specifies the ICCP parameters and communication requirements specific to the type of Market Participant, and describes the data to be exchanged for each Market Participant type.

Section 6, Data Available to All Market Participants describes data produced by ERCOT that is made available to any interested Market Participant.

Section 7, Data Calculated Locally by ERCOT describes values that ERCOT derives from telemetered data received from TSPs.

Attachment A through Attachment D provides forms to be used by Market Participants to initiate connections and services with ERCOT. The attachments are described where appropriate throughout the Handbook.

## Conventions Used in this Handbook

To enhance readability, a few simple formatting conventions are used in the Handbook. Data formats and information specifications are presented in the form of both variable data and fixed constants. The following font attribute conventions are used in the Handbook:

Variable fields display placeholders for values to be filled in with data that dependends on the Market Participant’s system.  Variable data is shown in this format.

Fixed constants are fields whose values are defined and do not change from system to system.  Constant values are shown in this format.

Some sections may lack detail that is being developed for inclusion in the Handbook, but not available as of the publication date. To avoid publication delay, comments are entered in this box style providing a summary of the information to be included. This is essentially a “TBD” comment.

The Handbook has been formatted for double-sided printing. Users are encouraged to take advantage of this document characteristic. The Handbook can also be printed using single-sided printing yielding high-quality results.

Although most of the document is in black & white, a number of illustrations are presented in color to facilitate the idea being illustrated. The color illustrations may not render well if printed in black & white.

## References

The references are listed here in two sections. The References to Standards section is primarily for those interested in delving deeper into ICCP technology. A study of these sources is not essential to the Market Participant’s ability to operate an ICCP node. It is assumed that the Market Participant’s ICCP vendor is familiar with the standards referenced in this section.

The ERCOT Publications section refers to additional documents that are essential to working with ERCOT, both for startup and day-to-day operation.

References to Standards:

IEC 870-6-503 Tase.2 Services and Protocol Version 2000

IEC 870-6-802 Tase.2 Object Models Version 2000

RFC 791 Internet Protocol (IP)

RFC 793 Transport Control Protocol (TCP)

RFC 1918 Address Allocation for Private intranets

ERCOT Publications:

Texas Nodal Protocols

Texas Nodal Market ICCP Certification Test Plan

Texas Nodal Market Operating Guide

Texas Nodal Enterprise Integration External Interfaces Specification

## Glossary

| Term | Definition |
| --- | --- |
| AIEF | Association Information Exchange Form. Used to establish the parameters necessary for Market Participants to successfully connect to the ERCOT systems. |
| Current Provider | Defines the supplier of the related value. Current Provider is a SCADA attribute which is either REMOTE, or LOCAL. When a value is received via ICCP, the Current Provider is the Market Participant and is marked REMOTE in SCADA. A value produced by the ERCOT operator, ERCOT’s state estimator, ERCOT’s calculation processor, or other ERCOT application is considered LOCAL. |
| Current Source | An ICCP attribute that specifies the device or process supplying the related value. The current source can be TELEMETERED – the related value has been obtained from a field measurement device or status detector, MANUAL – the related value has been obtained from an operator, CALCULATED – the related value has been produced by a calculation that is based on other possibly telemetered values, ESTIMATED – the related value has been produced by the State Estimator. |
| ICCP | Inter-Control Center Communication Protocol. A utility industry international standard communication protocol designed to facilitate data exchange between EMS/SCADA systems. ICCP is the common name for TASE.2, the Telecommunication Application Service Element defined in ISO/IEC 60870-6. TASE.2 is a utility industry specific definition of the use of the more general Manufacturing Message Specification (MMS) standardized in ISO/IEC 9506. |
| Normal Provider | An attribute maintained in SCADA that defines whether the related value is received via ICCP (REMOTE) or produced by ERCOT (LOCAL) under normal operating circumstances. See Current Provider. When the Normal Provider is not equal to the Current Provider, the related value is considered to have been replaced by the Current Provider. |
| Normal Source | In the ERCOT system, Normal Source is an attribute maintained in SCADA that defines the device or process that supplies the related value under normal operating circumstances. See Current Source. Although ICCP includes a Normal Source attribute, it is not used in the ERCOT system. When the Normal Source defined in SCADA is not equal to the Current Source received from ICCP, the related value’s Normal Source is considered to have been replaced by its Current Source. |
| Normal Value | An ICCP attributes that indicates whether the related status indication is NORMAL or ABNORMAL. |

# Connecting to the ERCOT Wide Area Network

## Network Topology Overview

ERCOT has implemented a TCP/IP based Wide Area Network (WAN) that supports the transfer of data between ERCOT and Market Participants. ERCOT Staff or its contractors monitor and manage the ERCOT Private WAN. ERCOT will pay for all costs associated with each WAN connection and pass those actual costs through the ERCOT accounting process to all Market Participants that connect to the WAN. All QSEs representing generation resources are required to communicate with ERCOT via the WAN. ERCOT will, from time to time, identify specific TSPs and any other QSEs (i.e. representing load resources) that are required to connect to the WAN. Any Market Participant required to connect must complete and submit the communication connection documentation as required in Section 4.2 for QSEs and Section 5.2 for TSPs.

Access to the ERCOT WAN by other Market Participants - (e.g. DSPs, Resources, Competitive Retailers and other QSEs) is not required but will be allowed. These Market Participants may use the Internet as an alternate method to exchange data with ERCOT.  The costs will be determined case-by-case, based on the communication options selected and bandwidth requirements of the Market Participant.  Market Participants interested in entering into such a WAN Access Service Agreement with ERCOT must complete and submit the communication connection documentation as required in Section 5.2 for each site that ERCOT will connect to.

The ERCOT private network will not allow the exchange of data between Market Participants.

ERCOT WAN is a redundant network comprised of the following network architectures:

- Private Frame Relay Network; and

- Private Point-to-Point DACS Network.

Figure 1 is an overview of the ERCOT WAN.

Figure 1 ERCOT Wide Area Network Overview

## Market Participant Site WAN Connections

The Figure 2 describes the equipment and connections supporting Operational, Engineering, and Market data exchange between ERCOT and Market Participants. This Market Participant Site Diagram illustrates the essential elements of the equipment and physical layer protocols used in the Market Participant’s interface to ERCOT.  All equipment shown in the figure below is located at the Market Participant’s site.

Figure 2 Market Participant Site Diagram

In the network infrastructure connection, ERCOT sets its line of demarcation to be a connection between a redundant pair of Ethernet Switches and the Market Participant’s firewall. It can be seen in Figure 2 that ERCOT provided equipment brings the redundant infrastructure into the Market Participant’s site that is necessary to meet the reliability requirements stated in the Nodal Protocols. On the Market Participant’s side of the line of demarcation, it is the Market Participant’s responsibility to provide an internal network infrastructure that also meets the Nodal Protocol’s communication reliability requirements.

The interconnecting Ethernet Switches form a Routing LAN that supports the routing of traffic over either the Frame Relay network or the DACS network. Traffic from the Market Participant’s system is exchanged over this network using ICCP, HTTPS, FTP, or other Application protocols as required by the various application services. This Handbook details connections using ICCP only.

## Equipment and Services Provided by ERCOT

ERCOT will provide to Market Participants the communication resources and services described in this section.

### Frame Relay Wide Area Network

ERCOT will be the single point of contact for all Frame Relay Network issues and shall:

- Supply and install fully configured and tested Customer Premises Equipment including routers, CSU/DSUs, LAN switch/hub and all support equipment for management purposes.

- Order and provision of local loop, network access point and transport.

- Design, configure, test, and install network monitoring and management service.

- Provide 24 hour network monitoring and management.

- Provide 24 X 7 maintenance, with 4-hour response, for all ERCOT equipment located at Market Participant site.

### Point-to-Point DACS Network

ERCOT will be the single point of contact for all DACS Network issues and shall:

- Supply and install fully configured and tested Customer Premises Equipment including routers, CSU/DSU’s, LAN switch/hub and all support equipment for management purposes.

- Order and provision of local loop, network access point and transport.

- Order and provision of T1 interface from CSU/DSU to Market Participant channel bank.

- Design, configure, test, and install network monitoring and management service.

- Provide 24 hour network monitoring and management.

- Provide 24 X 7 maintenance, with 4-hour response, for all ERCOT equipment located at Market Participant site.

## High Availability Data Connections

Figure 3 presents a high level overview of the ERCOT High Availability Data connection configuration.  Each site has fully redundant systems. The ICCP server architecture provides for two redundant subsystems: one for TSP communications and the other for QSE communications.  The overall architecture at each site has no single point of failure.

With this configuration, the EMS/SCADA system at each site performs dual sourcing data from Market Participants.  Through this feature the EMS/SCADA system acquires the data from both ICCP server sites simultaneously. This parallel operation increases the availability of the ICCP data acquisition functions to 99.9999%.  A second benefit is that a set of either EMS TSP or EMS QSE ICCP communication severs can be removed from service and the data is still available from the second set not only for the EMS/SCADA servers but also for the TSP and QSE systems.

The implications of the High Availability Data configuration for Market Participants are that ERCOT will receive live data at both the primary (Taylor) and backup locations (Austin) simultaneously. If the link to Taylor is detected as unavailable the system will receive information via the Austin ICCP server without action taken by ERCOT staff. This will increase the availability to meet ERCOT Nodal protocols and telemetry standards. Supporting this increased reliability will require that ERCOT establish two ICCP Associations (see Section 3.1) with each TSP and each QSE. The two Associations will be exchanging data simultaneously. Market Participant systems that support dual data sources can take advantage of this configuration by receiving data from both sites simultaneously.

Figure 3 High Availability Data Connections

## Network Security

All Market Participants directly connected to ERCOT (WAN) will be required to execute a connection agreement defining network security responsibilities. See Attachment A ERCOT WAN Connection Agreement.

# ICCP Conventions

## ICCP Connections

The protocol suite configured for the ERCOT ICCP network is OSI over TCP/IP using the Transport mapping layer specified in RFC 1006.  The complete profile for the ERCOT network is illustrated in Figure 4. Note in the figure that the line of demarcation distinguishes between ERCOT-provided equipment and Market Participant-provided equipment.

Figure 4 ICCP Network Protocol Suite

There will be variations at the physical layer (Layer 1) dependent on the Market Participant’s local communications architecture.  For example, the ICCP component of the Market Participant’s EMS could be connected to the network router via other connection types such as any variation of Ethernet connections or a serial link such as an HSSI, RS-232, etc. Market Participants establishing links will coordinate their configurations and schedules with ERCOT in preparation of link commissioning and testing.

### Establishing ICCP Associations

An ICCP Association is equivalent to a TCP connection.  ICCP Associations can be formed as “single-use” or “dual-use” Associations.  These Associations have to do with the client/server role taken by the Market Participant in its data exchange with ERCOT.  The Market Participant’s system acts as client when it receives data from ERCOT because of a request for the data.  The Market Participant’s EMS acts as a server when it sends data to ERCOT as requested.  A given ICCP node perceives its client and server roles to be separate and independent data exchange processes.  Environments exist where one side acts only as a client and the other acts only as a server, although this is unlikely to be the case for any ICCP node communicating with ERCOT.

A Single-use Association is one where one side of the Association always performs the client role and the other side performs the server role.  With Single-use Associations, two Associations are required in order for each side to act as both a client and a server.  With a Dual-use Association, one Association supports both ends acting as both client and server.  The concept is illustrated in Figure 5.

Figure 5 Types of ICCP Associations

ICCP vendors have taken different approaches to supporting Association use.  Some systems allow only one type while others allow both.  ERCOT supports both kinds of Associations in order to be compatible with any system.  However, to conserve resources and simplify system management, ERCOT requires Market Participants to establish Dual-use Associations if their ICCP nodes support it, even if they also support Single-use Associations.

The ICCP standard specifies that when Single-use Associations are established, the client always initiates the Association. For Dual-use Associations, the establishing side is determined by agreement.

ERCOT requires that ERCOT always establish Associations when a Dual-use Association is configured.

When Single-use Associations are implemented, ERCOT will establish the client-side Association with the Market Participant’s server function, and the Market Participant must establish the client-side Association with ERCOT’s server function in compliance with the ICCP standard.

Figure 6 and Figure 7 show how each conformance block operates over a set of Single-use Associations. The figures show that in all cases the client makes requests over the Association assigned to its client role, and receives data from the server over that same Association.  As the figures suggest, data exchange with ERCOT presently makes use of ICCP Conformance Blocks 1 and 2 only.

Figure 6 Single-use Association (ERCOT Server)

Figure 7 Single-use Association (Market Participant Server)

### Association Restrictions (Peer Communication)

The network architecture establishes Permanent Virtual Circuits (PVCs) between each Market Participant and ERCOT.  Although it is theoretically possible for Market Participants to establish peer Associations with each other, all such traffic would pass through routers located at ERCOT.  The ERCOT routers are configured to accept only traffic that originates with a Market Participant and is destined to ERCOT. Therefore, peer communication between Market Participants is not allowed via the ERCOT communications infrastructure.

### Association Identifiers

Association identifiers follow the ERCOT standard format described in this section.

Table 1 AP Title Format

| Field Name | Format (or Value) | Description |
| --- | --- | --- |
| ISO Prefix | 0002 | A standard ISO AP Title designator for applications using MMS. It stands for (joint-iso-ccitt) |
| Naming Hierarchy | 0016 | A standard designator indicating that the AP Title follows the country-based naming hierarchy. |
| Org ID | 0001 | ERCOT’s Organization Identifier. |
| Market Participant ID | 00AA 00AA 00AA 00AA | The Market Participant’s ICCP identifier. This identifier is also used in Domain names and Bilateral Table Names. The assigned Market Participants’ ICCP identifiers are included on the Association Information Exchange Form (AIEF). |
| Node ID | 00AA | The text representation of an integer designating the node number of the Market Participant’s ICCP node. The primary control center ICCP node is typically node “1” and the backup is typically node “2”. |
| Application ID | 0073 | This value specifies that ICCP is the application in use on this Association. |

The format shown as 00AA is a sequence of four integers.  The first two integers are zeros, and the last two are the decimal representation of an ASCII character.  As an example of a valid AP Title, ERCOT’s primary control center ICCP node would specify an AP Title of:

0002 0016 0001 0065 0067 0077 0069 0049 0073

The Market Participant ID and Node ID fields above represent the text string ACME1.

### Protocol Selectors

Protocol selectors are numerical identifiers for the Presentation Selector, Session Selector, and Transport Selector.  They are specified as two 8-bit decimal integers of the form NN NN, as in 00 01.

Although most systems specify 00 01 for all protocol selectors, the values required are dependent on the ICCP vendor’s system.  ERCOT’s local ICCP implementation does not require protocol selectors to be unique between ICCP nodes.  Therefore, ERCOT can support any protocol selector identification scheme as required by the various Market Participant systems. As a result, Market Participants are free to specify the desired protocol selector values on the AIEF.

### TCP Port Number

ICCP uses the TCP port number 102.  This is the IETF officially assigned TCP port for all connections to a system implementing RFC 1006. TCP Port 102 is the port number for the Transport Layer Service Access Point (TSAP) for Transport Class 0.

### System Connections

ERCOT operates the following systems:

- Primary ICCP Node at Taylor

- Backup ICCP Node at Austin

- Development System Node

The choice of network, circuit, and routers that traffic traverses is automatically determined by the routing protocols of the network redundancy architecture.  The intermediate system network elements operate under dynamic routing so that circuit failure recovery does not involve the end systems.  However, fixed IP addresses are assigned to each of ERCOT’s ICCP nodes. The IP addresses and AP Titles of the ERCOT ICCP nodes are provided on the AIEF. The Market Participant must respond to these addresses when processing Association Initiation requests.

In order to ensure that ERCOT establishes an Association with the correct Market Participant ICCP node, ERCOT will list IP addresses and AP Titles for Market Participant nodes in the following order on the AIEF:

- The primary node at the primary operating facility

- The secondary node at the primary operating facility

- The primary node at the secondary operating facility

- The secondary node at the secondary operating facility

Finally, ERCOT will list an additional IP address for the Market Participant’s development/test ICCP node. This node will not be included in the search list for operational nodes. However, the development/test node address is included in the ERCOT directory to support testing exercises with Market Participants during their development phase or for problem resolution.

A development/test ICCP node address will be assigned to a Market Participant whether or not the Market Participant actually has such an ICCP node. The AIEF includes a field for the Market Participant to indicate whether such an ICCP node exists. If a Market Participant later acquires a development/test ICCP node, this is the address ERCOT will use to access the node.

ERCOT assigns these IP addresses to the Market Participant’s ICCP nodes recognizing that the Market Participant may implement Network Address Translation (NAT) in their firewalls/routers. Using NAT, the Market Participant can assign internal IP addresses to the ICCP nodes that are compatible with the Market Participant’s corporate LAN addressing plan. Market Participants are strongly encouraged to implement such an address translation scheme inside the line of demarcation. Market Participants choosing not to implement NAT may have to contend with IP address conflicts.

## The ICCP Protocol

The ICCP documents listed in the references refer to the ICCP protocol standard. These documents provide a comprehensive definition of the ICCP protocol. Be aware that those documents are oriented toward ICCP protocol developers. Nevertheless, interested readers are encouraged to review the standard since an understanding of the ICCP architecture and terminology will facilitate communication with ICCP product vendors.

### Supported Features

During Association establishment, the client accesses the ICCP standard object named Supported_Features.  This object returns a bit string that specifies the ICCP Conformance Blocks supported in the server.  All ICCP implementations shall provide the features listed in Table 2 Required ICCP Supported Features.

Table 2 Required ICCP Supported Features

| Conformance Block | Bit Position |
| --- | --- |
| Block 1 | 0 |
| Block 2 | 1 |

### ICCP Version

ICCP defines a variable called TASE2_Version.  A client reads this variable after an Association is established to determine that the protocol versions will interoperate.  The present value of TASE2_Version is:

MajorVersionNumber = 1996	MinorVersionNumber = 8

All systems shall conform to this ICCP version. The variable TASE2_Version is VMD-specific, meaning that it is a system-wide global value not associated with any particular Domain. TASE2_Version should be considered as a hard-coded value imbedded in the ICCP vendor’s product release as opposed to a configuration parameter.

### Bilateral Tables

Bilateral Tables reflect a security mechanism ICCP defines to control access to data objects.  A Bilateral Table is a computer-generated reflection of a Bilateral Agreement.  A Bilateral Agreement is a formal document stating the objects a data owner is willing to provide to a data user. Bilateral Agreements and Bilateral Tables provide for contractual agreements between data exchange partners.

In practical application, few electric utility organizations implement the full methodology suggested by the ICCP standard for Bilateral Agreements.  Such a formal, contractual process is unrealistic due to the long lead-times that would be needed to effect a change in the objects exchanged between companies.  Instead of engaging in continuously negotiated data exchange contracts, ISOs typically develop a data privacy policy defining the acceptable use and accessibility of a data owner’s objects.  This eliminates the need for a separate detailed Bilateral Agreement.  Consequently, the ICCP Bilateral Table implements access controls that reflect the data privacy policy.

#### Bilateral Table Names

Various ICCP designs take different approaches to implementing Bilateral Tables.  Most systems do not implement a particular Bilateral Table data structure.  Rather, the definition of data objects includes access control attributes and the objects are assigned to Domains. Access control attributes combined with Domain assignment implement the concept of the Bilateral Table.  Regardless of the specific internal implementation, ICCP exposes a Bilateral Table identifier designed to ensure that the data object access list between ERCOT and a particular Market Participant is consistent. In the ICCP standard, this identifier is called the Bilateral Table Version. However, this Handbook refers to the ICCP Bilateral Table Version as the Bilateral Table Name.

The ERCOT naming standard for the Bilateral Table Name includes a text identifier and version number. The number portion of the Bilateral Table Name is typically incremented each time the Bilateral Agreement changes.  In the ERCOT system, the Bilateral Table Version number will rarely change.

Bilateral Table Name mismatches result in a failure to establish an Association.  Furthermore, Bilateral Table Name changes require Associations to be restarted.  ERCOT requires that Associations always function when physically possible. No procedure should be defined that would artificially cause an Association to fail.  The following Bilateral Table Version management procedure is designed to be consistent with this policy.

#### Bilateral Table Version Management

Bilateral Table Names have the form:

ERCT_pppp_nnnn

Where:

pppp is the company identifier for the Market Participant

nnnn is the Bilateral Table version number

The following example specifies a Bilateral Table Name for an Association between ERCOT and Acme:

ERCT_ACME_0001

The initial Bilateral Table Name is specified on the AIEF. There shall be only one Bilateral Table Name related to an Association between ERCOT and a given Market Participant. Specifically, the data object access list that ERCOT’s ICCP server provides to the Market Participant is identified under the same Bilateral Table Name as the data object access list that the Market Participant’s ICCP server provides to ERCOT. Once the Bilateral Table Name is defined, only the version number will subsequently change.

In order to facilitate frequent and rapid changes to the Bilateral Table, the Bilateral Table Version number will change infrequently.  Simply adding or deleting objects from a Market Participant’s Domain does not require a change to the Bilateral Table Version.

The first Bilateral Table Version shall always be 0001.  This version number will not change without the agreement of ERCOT.  Any change to the version number must be performed as part of a test similar to, though not as extensive as, the ICCP Certification Test.  The version number should only be changed when the data object list is modified so extensively that ERCOT and the Market Participant agree that it is in the best interest of both parties to re-synchronize the Bilateral Table.

The effect of this policy is to ensure that Associations can be established even if the Bilateral Table between the client and server disagree.  In this situation, when the client requests an object which it can no longer access, an object access error will be reported. The client can then simply remove the object’s definition either programmatically or by human intervention.

It is also possible that new items will be made available in the server of which the client is not aware.  To avoid this problem, the client can periodically retrieve the names of all the objects in the server to which the client has access.  The client can then compare this list with the objects defined in its database.  If any missing objects are discovered, and deemed by the client to be important, the client can add the objects to the database.

Be aware that whether or not a tool is available from the vendor to access the data object list, most changes are implemented as part of power system modeling. Updating the model involves a formalized exchange of model information between ERCOT and the Market Participant. There may be some exceptions where data not related to the model is exchanged, but any database changes important to the client will usually be conveyed by the people involved in making the changes.

### ICCP Conformance Blocks

This section describes the ICCP Conformance Blocks required to support the exchange of data between ERCOT and its Market Participants. The required ICCP Conformance Blocks are:

- Block 1 – Basic services including transfer of real-time data periodically.

- Block 2 – Transfer of real-time data by exception.

ICCP Conformance Blocks 1 and 2 are used to exchange real-time information about data elements. These data elements typically correspond to points in an EMS or SCADA system.  In ICCP-speak these points are called Data Value Objects.  Block 1 functionality is limited to direct value reads and periodic value reporting.  Block 2 adds reporting by exception and a variety of report generating triggers. Block 2 provides the most efficient mechanisms for real-time data exchange.

Although a client can read individual Data Value Objects, the greatest flexibility results from organizing points into Data Sets.  Data Sets are lists of Data Value Objects. Each Data Value Object referenced in a Data Set can be of any data type.

A Transfer Set is a data structure that specifies the conditions under which the server should send the content of a Data Set to the client. Transfer Set parameters are specified by the client. Parameters include such things as a reference to a Data Set (what is to be transferred), the conditions of transfer (when data should be transferred), and any limitations on the data report (such as RBE). After setting the Transfer Set parameters, the client creates the Transfer Set in the server, then starts the Transfer Set.

Transfer Set parameters and ERCOT usage standards are described in more detail in Section 3.3.

### ERCOT MMS PDU Size

ERCOT networking using ICCP shall support a maximum MMS PDU size of 32000 bytes. ICCP negotiates the actual maximum MMS PDU size during connection establishment.

## ICCP Data Exchange Conventions

This section discusses the data exchange conventions that are common to both TSPs and QSEs. The common conventions apply to Domain names, Data Set Names, and Data Object names for data that is provided to all Market Participants. Conventions for Data Object names that are unique to each Market Participant type and requirements for Transfer Set parameters can be found in the individual sections for each Market Participant type. Refer to Section 4.4 for QSE conventions and requirements, and Section 5.4 for TSP requirements and conventions.

### Domain Naming Conventions

Every ICCP server shall implement Domains.  These are conceptual containers for data to be exchanged between a particular client and server.  Domains are server specific. That is, a Domain is configured in a server to contain the values a particular client can access. The client must then know the name of the Domain in the server to which it has access in order to access those values. ERCOT implements a Domain for each Market Participant, and requires that each Market Participant acting as a server implement a Domain for ERCOT.

Domain names have the form:

ssss_cccc_tttt

Where:

ssss is the company identifier for the server

cccc is the company identifier for the client

tttt identifies the type of Market Participant

Values for tttt are assigned by ERCOT to each Market Participant.  Examples of these modifiers are:

NQSE identifies a Nodal Qualified Scheduling Entity

NTSP identifies a Nodal Transmission Service Provider

NREP identifies a Nodal  agent such as an aggregator

Shown here are example Domain Names for the client/server Association where the server is ERCOT and the client is Acme Services. Note that in this example Acme is both a Transmission Service Provider and a Qualified Scheduling Entity:

ERCT_ACME_NTSP

ERCT_ACME_NQSE

ERCOT stores the values accessible to Acme in each Domain as appropriate. Acme then includes the relevant Domain name in its access requests. Conversely, Acme’s system, when acting as a server would contain Domains for ERCOT configured as:

ACME_ERCT_NTSP

ACME_ERCT_NQSE

ERCOT then uses these names when accessing data from the Acme ICCP server(s).

ICCP vendors design their Domain architectures in various ways because the ICCP standard does not impose any specific design requirements on Domain implementation. Domain implementation in the ICCP server is usually straightforward, since a storage area for each ICCP client is obviously needed to segregate the values for one client from those for other clients. Each of these storage areas is distinguished by the Domain name .

An ICCP client does not require a separate storage area to contain the values accessed from individual servers. It is only required that the client provide the correct Domain name  when an access request is made. However, most ICCP vendors do set aside separate storage areas in the client so that a named Data Value Object accessed from one server won’t override the same object name accessed from another server. Because of this artifact of implementation, vendors sometimes adopt the terminology of a “remote” Domain versus a “local” Domain. Unfortunately, the meaning of “remote” versus “local” is nonstandard, so it may have the opposite meaning between different vendors.

Under the assumption that “local” means “in the server”, vendor documentation often speaks of creating a “remote” Domain and a “local” Domain having the same name. For example, a vendor might include in its ICCP documentation instructions to create a local Domain with the name ACME_ERCT_NTSP in Acme’s ICCP node providing transmission services. The documentation might also refer to the creation of a remote Domain with the same name in another ICCP node, such as ERCOT’s node. The local Domain simply means that the user is configuring a storage area in its server that will contain the values to be retrieved by the client node (ERCOT), which will refer to the name ACME_ERCT_NTSP.

The vendor may then discuss creating a remote Domain named ERCT_ACME_NTSP in the Acme node. In this case the Acme node, acting as a client, will retrieve data objects from the Domain named ERCT_ACME_NTSP in the ERCOT node which is acting as a server. These values will then be stored in a named region being set aside for that purpose.

The fact that vendors use the non-standard terms “local” and “remote”, and assign arbitrary meanings to the terms, is more confusing than helpful. The ICCP standard does assign well-defined meanings to the terms “client” and “server” and describes ICCP operations in those terms. Specifically, a “server” makes values available to interconnected computers, and a “client”, requests the available values. Servers define (and create) Domains and clients refer to them when requesting data. The illustration given in Figure 8 describes the intent of the standard and the effect of its interpretation by the product vendors.

Figure 8 Domain Names and Their Implementation

Domain Names are defined on the AIEF. ERCOT will assign Domain Names consistent with the naming standard specified here. The above discussion of Domains is given to avoid confusion about the information on the AIEF. The point here is that a Domain is always a server specification. Domains are never assigned to client nodes.

### Data Set Naming Conventions

Data Set names follow a convention similar to the Domain naming convention as follows:

ssss_cccc_nnnn

Where:

ssss is the company identifier for the server

cccc is the company identifier for the client

nnnn is a sequence number that uniquely defines the Data Set

If ERCOT were to create five Data Sets in the Acme server, the Data Sets would have the following names:

ACME_ERCOT_0001

ACME_ERCOT_0002

ACME_ERCOT_0003

ACME_ERCOT_0004

ACME_ERCOT_0005

A similar set of data sets created in the ERCOT server by Acme would have the following names:

ERCOT_ACME_0001

ERCOT_ACME_0002

ERCOT_ACME_0003

ERCOT_ACME_0004

ERCOT_ACME_0005

Clients create Data Sets in the server, so it would seem unnecessary to include the name of the server since every data set in a given server would include the name of the server.  However, doing so facilitates identification of Data Set locations when printed reports from different systems are combined in a single document.

### ICCP Object Naming Conventions for Data Available to All Market Participants

ERCOT makes available a set of system wide data available to all Market Participants. The ICCP Object naming convention for this data illustrated in the following name descriptor. Table 3 lists the ICCP object names assigned to each of the system wide data objects.

cccctttsssssssseeeeeeeedddduuuu

Where:

cccc	is the 4-character company name

ttt	is the 3-character type descriptor

ssssssss	is the 8-character station name

eeeeeeee	is the 8-character equipment name

dddd	is an 8-character data descriptor

uuuu	is the 4-character unit of measure

Table 3 ICCP Object Names for Data Available to All Market Participants

| Data Scope | Type Descriptor | Data | Data Descriptor | Unit of Measure | ICCP Data Type | ICCP Object Name Example cccctttsssssssseeeeeeeedddduuuu |
| --- | --- | --- | --- | --- | --- | --- |
| System Wide | SYS | Responsive Reserve Capacity from Generation Resources | RRGN | MW | RealQ | ERCTSYSERCOT___ERCOT___RRGNMW__ |
|  |  | Responsive Reserve Capacity from Load Resources excluding Controllable Load Resources | RRLD | MW | RealQ | ERCTSYSERCOT___ERCOT___RRLDMW__ |
|  |  | Responsive Reserve Capacity from Controllable Load resources | RRCL | MW | RealQ | ERCTSYSERCOT___ERCOT___RRCLMW__ |
|  |  | Non-Spinning Reserve available from On-Line Generation Resources with Energy Offer Curves | NSOG | MW | RealQ | ERCTSYSERCOT___ERCOT___NSOGMW__ |
|  |  | Non-Spinning Reserve available from undeployed Load Resources | NSUD | MW | RealQ | ERCTSYSERCOT___ERCOT___NSUDMW__ |
|  |  | Non-Spinning Reserve available from Off-Line Generation Resources | NSOF | MW | RealQ | ERCTSYSERCOT___ERCOT___NSOFMW__ |
|  |  | Non-Spinning Reserve available from Resources with Output Schedules | NSNS | MW | RealQ | ERCTSYSERCOT___ERCOT___NSNSMW__ |
|  |  | Undeployed Reg-Up | URUP | MW | RealQ | ERCTSYSERCOT___ERCOT___URUPMW__ |
|  |  | Undeployed Reg-Down | URDN | MW | RealQ | ERCTSYSERCOT___ERCOT___URDNMW |
|  |  | Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | ACUP | MW | RealQ | ERCTSYSERCOT___ERCOT___ACUPMW__ |
|  |  | Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | ACDN | MW | RealQ | ERCTSYSERCOT___ERCOT___ACDNMW__ |
|  |  | Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | CUP | MW | RealQ | ERCTSYSERCOT___ERCOT___CUP_MW__ |
|  |  | Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | CDN | MW | RealQ | ERCTSYSERCOT___ERCOT___CDN_MW__ |
|  |  | Total ERCOT Load | ERLD | MW | RealQ | ERCTSYSERCOT___ERCOT___ERLDMW__ |
|  |  | Total ERCOT Generation | ERGN | MW | RealQ | ERCTSYSERCOT___ERCOT___ERGNMW__ |
|  |  | Total ERCOT Generation Operating Reserve | EOPR | MW | RealQ | ERCTSYSERCOT___ERCOT___EOPRMW__ |

## Data Quality

ERCOT recognizes the following categories of ICCP data quality:

- Validity

- Current Source

- Normal Value

Validity is the attribute that SCADA systems treat as a point’s quality code. The Validity attribute values provided in ICCP are VALID, NOT_VALID, HELD, and SUSPECT. Each SCADA system vendor must translate between these attribute values and some meaningful equivalent SCADA quality code. This section on data quality includes an extensive definition of the kind of translation between SCADA quality codes and the ICCP Validity attribute that is necessary for consistency of meaning between ERCOT’s SCADA system and those of the Market Participants.

Current Source is an attribute that identifies how a measured value or status indication is acquired. The Current Source can be any of: TELEMETERED, CALCULATED, ESTIMATED, or MANUAL. The Current Source of a value can change at any time. If a SCADA system knows the normal source of a value, ICCP’s Current Source attribute can be used to determine whether or not the value has been replaced, and what source replaced it.

The Normal Value attribute is supported for status indications only. This attribute has the values NORMAL, or ABNORMAL. The Normal Value attribute allows the data provider to specify whether the state of a status point is considered to be normal, or off-normal.

ERCOT also distinguishes between a value received from a Market Participant and a value produced by ERCOT (referred to here as the Provider). Table 4  and Table 5 illustrate ERCOT’s treatment in its SCADA system of the various combinations of Normal Source, Current Source, Normal Provider and Current Provider. The tables tell a simple story. They show that when the provider is a Market Participant, REMOTE is set in the ERCOT SCADA database; otherwise REMOTE is not set. If the Current Provider is equal to the Normal Provider and the Current Source is equal to the Normal Source, REPLACED is not set. Otherwise, REPLACED is set.

The only exception is when a Market Participant sends a Current Source as TELEMETERED, and ERCOT has the Normal Source configured as MANUAL. In this case MANUAL is assumed, so REPLACED is not set. This exception is included to support systems that always report a value as TELEMETERED even if the Market Participant’s operator always manually enters the value.

In Table 4 ERCOT is not shown as a Normal Provider because there is no case where a Market Participant (as the Current Provider) would override a value that is always produced by ERCOT. In Table 5 the TELEMETERED column has been eliminated because there is no case where ERCOT (as the Current Provider) would override any value with a value that has been telemetered by ERCOT. ERCOT does not do telemetry. All telemetered values are acquired from Market Participants. Entries in the tables showing n/a indicate other combinations that are not expected to arise.

Table 4 ERCOT's Determination of a REPLACED Value when Current Provider is Market Participant

| Normal Provider | ICCP Normal Source Attribute | ICCP Current Source Attribute (Current Provider is Market Participant) |  |  |  |
| --- | --- | --- | --- | --- | --- |
|  |  | TELEMETERED | CALCULATED | ESTIMATED | MANUAL |
| MP | TELEMETERED (Field Telemetered) | REMOTE GOOD | REMOTE CALC_REPLACED | REMOTE SE_REPLACED | REMOTE MANUALLY_REPLACED |
| MP | CALCULATED | n/a | REMOTE GOOD | REMOTE SE_REPLACED | REMOTE MANUALLY_REPLACED |
| MP | ESTIMATED (State Estimator) | n/a | n/a | REMOTE GOOD | REMOTE MANUALLY_REPLACED |
| MP | MANUAL (MP Operator Entered – Non-Field Telemetered) | REMOTE GOOD | REMOTE CALC_REPLACED | REMOTE SE_REPLACED | REMOTE GOOD |

Table 5 ERCOT's Determination of a REPLACED Value when Current Provider is ERCOT

| Normal Provider | ICCP Normal Source Attribute | ICCP Current Source Attribute (Current Provider is ERCOT) |  |  |
| --- | --- | --- | --- | --- |
|  |  | CALCULATED | ESTIMATED | MANUAL (ERCOT Operator Entered) |
| MP | TELEMETERED (Field Telemetered) | CALC_REPLACED | SE_REPLACED | MANUALLY_REPLACED |
| MP | CALCULATED | CALC_REPLACED | SE_REPLACED | MANUALLY_REPLACED |
| MP | ESTIMATED (State Estimator) | CALC_REPLACED | SE_REPLACED | MANUALLY_REPLACED |
| MP | MANUAL (Operator Entered – Non-Field Telemetered) | CALC_REPLACED | SE_REPLACED | MANUALLY_REPLACED |
| ERCOT | TELEMETERED (Field Telemetered) | CALC_REPLACED | SE_REPLACED | MANUALLY_REPLACED |
| ERCOT | CALCULATED | GOOD | SE_REPLACED | MANUALLY_REPLACED |
| ERCOT | ESTIMATED (State Estimator) | n/a | GOOD | MANUALLY_REPLACED |
| ERCOT | MANUAL (Operator Entered – Non-Field Telemetered) | CALC_REPLACED | SE_REPLACED | GOOD |

Table 6 ERCOT SCADA Quality Code and ICCP Validity Code Translation to SCADA Quality Codes

| Current Source | ICCP Validity |  |  |  |
| --- | --- | --- | --- | --- |
|  | NOT_VALID | HELD | SUSPECT | VALID |
| TELEMETERED | BAD | OLD (Stale) | OLD (Stale) | GOOD |
| CALCULATED | BAD | OLD (Stale) | OLD (Stale) | GOOD |
| ESTIMATED | n/a | n/a | n/a | GOOD |
| MANUAL | n/a | (no SCADA translation) | n/a | GOOD |

In addition to the various “REPLACED” codes, the quality of the value exchanged is also provided. Table 6 shows the translation of the ICCP Validity attribute into SCADA quality codes. The combination of Source, Provider, and Validity may cause multiple flags to be set for a point. The combination is capable of telling a rich story about the related value.

### Quality Codes Illustrated

Additional scenarios will be added, including scenarios for data sent from ERCOT to the Market Participant.

### Detail Quality Code Definitions

Although tables and illustrations are helpful in understanding quality code translation processes, vendors implementing translation algorithms need to know the specific criteria that drive the translation. Table 7 through Table 10 describes in detail the conditions under which the Market Participant sets the various ICCP Data Object attributes for status indications and measured values sent to ERCOT. Each table discusses the attribute requirements for a different Normal Source. In a similar way Table 11 through Table 14 specifies the circumstances under which ERCOT sets ICCP Data Object attributes for status indications and measured values sent to Market Participants.

#### ICCP Quality Codes from Market Participants to ERCOT

Table 7 ICCP Attributes for Telemetered Points from Market Participants to ERCOT

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The measured value or status indication is valid and can be trusted by ERCOT. |
|  | HELD | Point has been taken off scan by the Market Participant or otherwise removed from service. The value or status indication associated with this ICCP quality code must be the last good value obtained by the Market Participant, or a value that has been substituted by the Operator (see Current Source / MANUAL) below. ERCOT expects that when the Market Participant’s Operator manually enters a value or state, the point is also taken off scan. |
|  | SUSPECT | Any of the following: old value or state due to telemetry failure or failure to acquire a new value within the specified scan time (stale), considered suspect by the data owner, or otherwise should not be considered by ERCOT to be current. The measured value or status indication associated with this ICCP quality code must be the last good value obtained by the Market Participant. |
|  | NOT_VALID | The measured value or status indication is invalid due to data acquisition/conversion errors or the initial value has never been established. The measured value or status indication associated with this ICCP quality code must be the last good value obtained by the Market Participant. If the measured value or status indication has never been initialized, the value or status indication associated with this quality code must be a predefined default value. |
| Current Source | TELEMETERED | The measured value or status indication was acquired from a field device, which is the normal source of this value or status indication. |
|  | CALCULATED | Although the measured value or status indication is normally acquired from a field device, it has been replaced by a calculated value. |
|  | MANUAL | Although the measured value or status indication is normally acquired from a field device, it has been replaced by the Market Participant’s Operator. |
|  | ESTIMATED | Although the value or status indication is normally acquired from a field device, it has been replaced by the Market Participant’s State Estimator. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

Table 8 ICCP Attributes for Calculated Points from Market Participants to ERCOT

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The value or status indication is valid and can be trusted by ERCOT. |
|  | HELD | Must be set if any of the points on which the calculated value is based have been taken off scan by the Market Participant or otherwise removed from service. |
|  | SUSPECT | Must be set if any of the points on which the calculated value is based are any of the following: old value or state due to telemetry failure or failure to acquire a new value within the specified scan time (stale), considered suspect by the data owner, or otherwise should not be considered by ERCOT to be current. |
|  | NOT_VALID | Must be set if any of the points on which the calculated value is based is invalid due to data acquisition/conversion errors or the initial value has never been established. NOT_VALID may also be set if the calculation processor has not yet populated this point with a value. In this case, the value or status indication associated with this quality code must be a predefined default value. |
| Current Source | TELEMETERED | See Table 7. ERCOT does not anticipate a condition where a calculated point would be replaced with a telemetered value or status indication. |
|  | CALCULATED | The Validity attribute is processed as discussed above. No additional processing is applied. |
|  | MANUAL | The Validity attribute is processed as discussed above. The point will also be considered as Manually Replaced by the Operator. |
|  | ESTIMATED | ERCOT does not anticipate a condition where a normally calculated value would be replaced by the State Estimator. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be abnormal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

Table 9 ICCP Attributes for Manually Entered Points from Market Participants to ERCOT

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The value or status indication is valid and can be trusted by ERCOT. |
|  | HELD | HELD is never set when the Normal Source is also MANUAL. |
|  | SUSPECT | SUSPECT is never set. |
|  | NOT_VALID | When an Operator enters a value, NOT_VALID is never set. However, if NOT_VALID is received by ERCOT for a normally Operator Entered value or status indication, ERCOT will interpret this to mean that the Operator has not yet entered a value for this point. |
| Current Source | TELEMETERED | ERCOT does not anticipate a condition where a normally Operator entered value would be replaced with a telemetered value or status indication. However, if the Market Participant reports the Current Source as TELEMETERED, ERCOT will consider the Current Source as MANUAL. |
|  | CALCULATED | ERCOT does not anticipate a condition where a normally Operator Entered value would be replaced by an output of the calculation processor. |
|  | MANUAL | The Validity attribute is processed as discussed above. No additional processing is applied. |
|  | ESTIMATED | ERCOT does not anticipate a condition where a normally Operator-entered value would be replaced by the State Estimator. |
| Normal Source |  | The ICCP attribute Normal Source is not processed by ERCOT. The Normal Source of a point is configured locally in the ERCOT real-time SCADA database. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be abnormal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

Table 10 ICCP Attributes for State Estimated Points from Market Participants to ERCOT

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The value or status indication is valid and can be trusted by ERCOT. |
|  | HELD | Indicates that the Operator or other process has prevented the State Estimator from populating this point. |
|  | SUSPECT | The State Estimator normally would not set SUSPECT. However, if a Market Participant’s system sends the SUSPECT quality, ERCOT will interpret this as meaning that the Market Participant’s State Estimator failed to produce a result that can be trusted by ERCOT. The value or status indication associated with this point should be the last good value produced by the State Estimator. |
|  | NOT_VALID | The Market Participant’s State Estimator is not expected to set NOT_VALID. However, if a Market Participant’s system sends the NOT_VALID quality, ERCOT will interpret this as meaning that the Market Participant’s State Estimator has not yet populated this point with a resultant value or status indication. In this case, the value or status indication associated with this quality code must be a predefined default value. |
| Current Source | TELEMETERED | ERCOT does not anticipate a condition where a normally State Estimated point would be replaced with a telemetered value or status indication. |
|  | CALCULATED | ERCOT does not anticipate a condition where a normally State Estimated value would be replaced by an output of the calculation processor. |
|  | MANUAL | The Validity attribute is processed as discussed above. The point will also be considered as Manually Replaced by the Operator. |
|  | ESTIMATED | The Validity attribute is processed as discussed above. No additional processing is applied. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be abnormal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

#### ICCP Quality Codes from ERCOT to Market Participants

Table 11 ICCP Attributes for Telemetered Points from ERCOT to Market Participants

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The measured value or status indication is valid and can be trusted by the Market Participant. |
|  | HELD | Indicates that the related point has been removed from scan by ERCOT. |
|  | SUSPECT | The measured value or status indication is OLD (stale) because it has been removed from scan either by ERCOT or the data provider. The measured value or status indication may also have been received from the data provider in any of the following conditions: old due to telemetry failure or failure to acquire a new value within the specified scan time (stale). The measured value or status indication associated with this ICCP quality code will be the last good value obtained by the ERCOT. |
|  | NOT_VALID | The measured value or status indication is invalid due to data acquisition/conversion errors experienced by the data provider or the initial value has never been established. The measured value or status indication associated with this ICCP quality code will be the last good value obtained by the data provider. If the measured value or status indication has never been initialized, the value or status indication associated with this quality code will be a predefined default value. |
| Current Source | TELEMETERED | Always set. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

Table 12 ICCP Attributes for Calculated Points from ERCOT to Market Participants

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The value or status indication is valid and can be trusted by Market Participant. |
|  | HELD | The point has been inhibited from being updated by the calculation processor. |
|  | SUSPECT | Set if any of the points on which the calculated value is based SUSPECT. |
|  | NOT_VALID | Set if any of the points on which the calculated value is based are NOT_VALID. NOT_VALID may also be set if the calculation processor has not yet populated this point with a value. In this case, the value or status indication associated with this quality code will be a predefined default value. |
| Current Source | CALCULATED | Always set. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be abnormal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

Table 13 ICCP Attributes for Manually Entered Points from ERCOT to Market Participants

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The value or status indication is valid and can be trusted by Market Participant. |
|  | HELD | Never set. |
|  | SUSPECT | Never set. |
|  | NOT_VALID | When an Operator enters a value, NOT_VALID is never set. However, if NOT_VALID is received by ERCOT from a data provider, ERCOT will interpret this to mean that the data provider’s Operator has not yet entered a value for this point. Points that are normally entered by the ERCOT Operator will also produce NOT_VALID if the ERCOT Operator has not yet entered a value for the point. |
| Current Source | MANUAL | Always set. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be abnormal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

Table 14 ICCP Attributes for State Estimated Points from ERCOT to Market Participants

| ICCP Quality Class | ICCP Attribute value to be sent from Market Participant to ERCOT | Condition under which ICCP Attribute value is to be sent to ERCOT. |
| --- | --- | --- |
| Validity | VALID | The value or status indication is valid and can be trusted by Market Participant. |
|  | HELD | Indicates that the related point has been inhibited from being updated by the State Estimator. |
|  | SUSPECT | The State Estimator normally would not set SUSPECT. However, if a data provider’s system sets the SUSPECT quality, ERCOT will interpret this quality code as meaning that the Market Participant’s State Estimator failed to produce a result that can be trusted by ERCOT. ERCOT will pass SUSPECT to the receiving Market Participant along with the last good value produced by the data provider’s State Estimator. |
|  | NOT_VALID | Neither the data provider’s nor ERCOT’s State Estimator is expected to set NOT_VALID. However, if a data provider’s system sets NOT_VALID, ERCOT will interpret this quality code as meaning that the data provider’s State Estimator has not yet populated this point with a resultant value or status indication. ERCOT will also produce NOT_VALID if ERCOT’s State Estimator has not yet populated this point with a resultant value. In this case, the value or status indication associated with this quality code will be a predefined default value. |
| Current Source | ESTIMATED | Always set.. |
| Normal Value | NORMAL | For status indications, the state reported is considered to be normal. For other data types, the Normal Value attribute has no meaning. |
|  | ABNORMAL | For status indications, the state reported is considered to be abnormal. For other data types, the Normal Value attribute has no meaning. |
| COVClass = COV | COVCounter > 0 | Number of state changes that occurred between acquisitions of a status point. Use of COV is optional. As an alternative, each state change can be sent to ERCOT without the COV attribute (COVClass = NOCOV) |

## Data Semantics

In order to assure full interoperability between ERCOT and its Market Participants, certain data values must have common semantics.  These semantics are defined in this section.  Each Market Participant’s system shall provide the required data conversion functions to ensure that values are sent to ERCOT with the meanings defined here.

### Status Indication Semantic Conventions

The convention for status values shall be as defined in Table 15.

Table 15 Status Indication Semantic Conventions

| 00 | 01 | 10 | 11 | Device |
| --- | --- | --- | --- | --- |
| Between | Tripped | Closed | Invalid | Recloser |
| Between | Off | On | Invalid | Recloser |
| Invalid | Off | On | Invalid | Breaker |
| Invalid | Open | Closed | Invalid | Breaker |
| Invalid | Auto | Manual | Invalid | Any |
| Invalid | Normal | Alarm | Invalid | Any |
| Invalid | Local | Remote | Invalid | Any |
| Invalid | Raise | Lower | Invalid | Transformer |
| Invalid | Not Ready | Ready | Invalid | Any |
| Invalid | Off Line | Available | Invalid | Any |

### Energy and Reactance Value Semantic Conventions

Values representing energy and reactance are to be provided in the units defined in Table 16.

Table 16 Energy and Reactance Semantic Conventions

| Value Semantics | Unit of Measure |
| --- | --- |
| Power | Megawatts (MW) |
| Energy | Megawatt-hours (MWh) |
| Reactance | Megavar (MVAR) |
| Loss | Megawatt-hour (MWh) |
| Frequency | Cycles per Second (Hz) |
| Voltage | Kilovolts (kV) |
| Penalty Factor | Actual factor value |

### Sign Conventions

Table 17 ERCOT ICCP Data Sign Conventions

| Equipment Type | Measurement | Sign Convention |
| --- | --- | --- |
| Bus | Voltage | Always positive |
|  | Frequency |  |
| Transformer | Megawatts | Positive = flow into transformer |
|  | Megavars |  |
| Line | Megawatts | Positive = flow out of substation |
|  | Megavars |  |
| Reactor or Capacitor | Megavars | Positive = supplying vars |
| Circuit Breaker | Megawatts | Positive = flow out of bus section into equipment |
|  | Megavars |  |
| Load | Megawatts | Always negative |
|  | Megavars |  |
| DC Injection | Megawats | Positive = flow out of substation |

# QSE Connection Requirements

## QSE Communication Requirements

Any QSE facility, whether primary or backup, involved in the transfer of the data identified in Section 4.4 will be required to connect directly to the ERCOT Frame Relay and Point-to-Point networks. If a TSP and QSE share the same EMS at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TSP and QSE share a centralized PBX, separate OPX circuits will be terminated for each Market Participant.  The Hotline is required for each Market Participant and will not be allowed to connect through the PBX system.

Telemetry performance measures required by the protocols will always measure the performance of the entity responsible for the data as established in the protocols. Each entity using others to transfer their data to or from  ERCOT must be responsible for the performance of that data regardless of the path the data takes to get to ERCOT.  Likewise, scan rate requirements in the protocols measure the data update requirement from the field device to ERCOT with no allowance for delays of shared data paths.

A QSE is required to provide the following communication resources to support the connection to the ERCOT private network:

- Provide an analog business phone line or PBX analog extension for trouble-shooting and maintenance of equipment.

- Provide a height of 24” of rack space in a 19” wide rack.

- Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above.

- Provide building wiring from circuit termination to equipment rack.

- Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility.

- Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors.

- Provide on site personnel to escort ERCOT employees or contractors.

- Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN.

- Market Participant will be required to sign a security connection agreement with ERCOT.

- Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site. Market Participants are responsible for their own security through this connection.

- Provide a channel bank with at least one T1 interface, 1 ringing generator, and 4 FXS ports. Connect the FXS (e.g. PBX, key system).  On the digital T1 stream, levels for voice are zero dpm for transmit and receive.

- Hotline must be a 500 set not attached to the Market Participant’s Phone System.

- Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended.

- Provide ERCOT internal IP addressing scheme for network design. This will be kept confidential.

## QSE Implementation Procedures

QSEs are required to use the ERCOT private network for exchanging data with ERCOT. The data to be exchanged is defined in Section 4.4. In order to initiate the connection process, QSEs must complete and submit the following documents to ERCOT:

Attachment A ERCOT WAN Connection Agreement

Attachment B Market Participant WAN Circuit Installation Site Survey

Attachment C Market Participant WAN Equipment Installation Site Survey

The Circuit and Equipment Site Surveys must be completed for each site that ERCOT will connect to.

ERCOT will perform circuit and equipment installation at QSE sites in coordination with the QSE. QSEs should plan for adequate time for ERCOT’s procurement, installation, and testing of communication equipment.

Although you may fax or e-mail the required documents, you must also submit all original documentation to:

ERCOT
		Attn: Ted Hailu, Client Relations Manager
		2705 West Lake Drive
		Taylor, Texas 76574
		Phone: (512) 248-3873
		Fax: (512) 248-3886
		thailu@ercot.com

Revise above contact information to be current with the Texas Nodal Market point of contact.

## QSE Association Information Exchange Form (AIEF)

Electric Reliability Council of Texas

Association Information Exchange Form (AIEF)

| Date Completed by Market Participant: |  |
| --- | --- |
| Market Participant Company Name: |  |
| Contact Name: |  |
| Mailing Address: |  |
| City, State, Zip: |  |
| Phone: |  |
| Email: |  |

| ERCOT Name: | Electric Reliability Council of Texas |
| --- | --- |
| Contact Name: | David Dickenson |
| Mailing Address: | 2705 West Lake Drive |
| City, State, Zip: | Taylor, Texas 76574 |
| Phone: | (512) 248-6528 |
| Email: | ddickenson@ercot.com |

Version: 1.0

Instructions

This form is used to exchange the information needed by ERCOT and you, the Market Participant, for configuring ICCP nodes. The form is designed for electronic transmittal (via email). ERCOT sends this form to you in response to your request for a connection.

You request a connection by filling out Attachments A, B, C, and D and submitting them to ERCOT. Most of the information on the AIEF is defined by ERCOT on the basis of the Site Survey information you provided with your Connection Agreement. ERCOT sets up the addresses and other parameters required to complete the connection, then ERCOT sends the AIEF to you. The information provided by ERCOT is shown in the fields shaded in light gray. You complete the unshaded fields and return the form to ERCOT.

The AIEF consists of four forms, at least two of which must be completed. The forms are:

| Network Information Form | This form provides information applicable to all ICCP nodes. It includes platform identification, Domain and Bilateral Table names and Association type. This form must be completed. |
| --- | --- |
| Primary Site ICCP Node Form | This form provides information specific to the primary and backup ICCP nodes located at your primary operating site. Most of the information on this form provides addressing information. This form must be completed. If you have a third ICCP node at the primary site, identify it on the Secondary Site ICCP node Form. It will be evident by the information you provided in your Site Surveys that the third node is located at this site. |
| Secondary Site ICCP Node Form | This form provides information specific to the primary and backup ICCP nodes located at your secondary operating site. This form contains the same information fields as the Primary Site ICCP Node Form. You may refer to this site as your backup or disaster recovery site. We use the term “secondary site” to avoid confusion with the backup ICCP node. This form must be completed if you are installing ICCP nodes at a secondary site. If you have a development or training system at a secondary site that you wish to use as an operational backup (and no other backup site), then this ICCP node is considered by ERCOT to be your secondary site node. |
| Alternate Site ICCP Node Form | This form provides information specific to one or more ICCP nodes that may be located at a third facility. Some Market Participants may have a development or training system not located at the primary or secondary sites, but in addition to them, that they might use as a third level of backup. ERCOT does not maintain such a site. Note that if your development or training system will not be used as an operational backup, do not identify it on this form. Such ICCP nodes do not need to be known by ERCOT. |

Once ERCOT receives your completed AIEF, ERCOT will configure its ICCP nodes to communicate with yours. However, the links will remain turned off (disabled) until you communicate your readiness to perform the Certification Tests.

The AIEF cover page contains fields for you to enter your contact information. This information should apply to the person in your company who will be working with ERCOT to configure the ICCP nodes and validate the connection. Instructions for completing each of the form fields are given in the forms.

Table 18 QSE Network-wide Information Form

| Form Entry Description | ERCOT | Market Participant |
| --- | --- | --- |
| ICCP Vendor: | Areva |  |
| Vendor Software Version: | e-terracomm ver 2.4 |  |
| ICCP Server Hardware Platform: | IBM |  |
| ICCP Server Operating System: | Windows 2003 Server |  |
| Domain Name: The Domain name which each company’s client will use to access the other company’s server. For example, the domain name listed for ERCOT is the name that the Market Participant’s client will use to access ERCOT’s ICCP server. Conversely, the Domain name shown in the Market Participant column, is the Domain name the Market Participant must assign to ERCOT’s domain in the Market Participant’s ICCP server. | ERCT_XXXX_ISO | XXXX_ERCT_NQSE |
| Association Type: Specify either “Single” or “Dual”. If the Market Participant’s ICCP product is capable of Dual use associations, then “Dual” must be specified and configured. Enter “Single” in the Market Participant’s column only if Dual cannot be supported. ERCOT will configure its ICCP nodes to match the specification you enter here. Therefore you can assume that ERCOT has placed the same specification in the ERCOT column. ERCOT will be the initiator when the Association type is specified as “Dual”. |  | Dual |
| Initial Bilateral Table Name: This is the assigned Bilateral Table Name according to the ERCOT naming standard, including the Bilateral Table Version number. | ERCT_XXXX_0001 | ERCT_XXXX_0001 |

Table 19 QSE Primary Site ICCP Node Form

| Form Entry Description | ERCOT Primary ICCP Node | ERCOT Backup ICCP Node | Market Participant Primary ICCP Node | Market Participant Backup ICCP Node |
| --- | --- | --- | --- | --- |
| ICCP Node Name: The name by which people refer to this Node. This name is not transmitted during any ICCP transactions, but is only used to facilitate verbal communication between company personnel. | ERPOAGA | ERPOAGB | Filled in by Market Participant | Filled in by Market Participant |
| ICCP Node IP Address: This is the IP address assigned by ERCOT to access the ICCP node on the company internal LAN. The Market Participant may assign this IP address directly to the applicable ICCP node, or use Network Address Translation in a Market Participant-provided router or firewall. | 192.168.XX.80 | 192.168.XX.81 | Market Participant’s Real address xxx.xxx.xxx.xxx mapped to 192.168.XX.20 | Market Participant’s Real address xxx.xxx.xxx.xxx mapped to 192.168.XX.21 |
| AP Title: The Application Process Title given to the ICCP application instance. Note that the assignments follow the standard notation defined in the NICD as individual parameters. The format for entry of the AP Title in your system will depend on your vendor’s configuration user interface. | 2 16 1 69 82 67 84 49 73 | 2 16 1 69 82 67 84 50 73 | 2 16 1 XX XX XX XX 49 73 | 2 16 1 XX XX XX XX 50 73 |
| AE Qualifier: This parameter is required on some ICCP implementations if ICCP is communicating with multiple clients and/or servers. Refer to your vendor documentation to determine if a value is required. | 1 | 1 | 1 | 1 |
| Presentation Selector (PSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 |
| Session Selector (SSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |
| Transport Selector (TSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |

Table 20 QSE Secondary Site ICCP Node Information

| Form Entry Description | ERCOT Primary ICCP Node | ERCOT Backup ICCP Node | Market Participant Primary ICCP Node | Market Participant Backup ICCP Node |
| --- | --- | --- | --- | --- |
| ICCP Node Name: The name by which people refer to this Node. This name is not transmitted during any ICCP transactions, but is only used to facilitate verbal communication between company personnel. | ERPOAGC | ERPOAGD | Filled in by Market Participant | Filled in by Market Participant |
| ICCP Node IP Address: This is the IP address assigned by ERCOT to access the ICCP node on the company internal LAN. The Market Participant may assign this IP address directly to the applicable ICCP node, or use Network Address Translation in a Market Participant-provided router or firewall. | 192.168.1XX.80 | 192.168.XX.81 | Market Participant’s Real address xxx.xxx.xxx.xxx mapped to 192.168.XX.20 | Market Participant’s Real address xxx.xxx.xxx.xxx mapped to 192.168.XX.21 |
| AP Title: The Application Process Title given to the ICCP application instance. Note that the assignments follow the standard notation defined in the NICD as individual parameters. The format for entry of the AP Title in your system will depend on your vendor’s configuration user interface. | 2 16 1 69 82 67 84 51 73 | 2 16 1 69 82 67 84 52 73 | 2 16 1 XX XX XX XX 49 73 | 2 16 1 XX XX XX XX 50 73 |
| AE Qualifier: This parameter is required on some ICCP implementations if ICCP is communicating with multiple clients and/or servers. Refer to your vendor documentation to determine if a value is required. | 1 | 1 | 1 | 1 |
| Presentation Selector (PSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 |
| Session Selector (SSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |
| Transport Selector (TSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |

Table 21 QSE Alternate Site ICCP Node Information

| Form Entry Description | ERCOT Test ICCP Node | Market Participant Primary ICCP Node | Market Participant Backup ICCP Node |
| --- | --- | --- | --- |
| ICCP Node Name: The name by which people refer to this Node. This name is not transmitted during any ICCP transactions, but is only used to facilitate verbal communication between company personnel. | ERTOAGA | Filled in by Market Participant | Filled in by Market Participant |
| ICCP Node IP Address: This is the IP address assigned by ERCOT to access the ICCP node on the company internal LAN. The Market Participant may assign this IP address directly to the applicable ICCP node, or use Network Address Translation in a Market Participant-provided router or firewall. | 192.168.XX.30 | Market Participant’s Real address xxx.xxx.xxx.xxx mapped to 192.168.XX.20 | Market Participant’s Real address xxx.xxx.xxx.xxx mapped to 192.168.XX.21 |
| AP Title: The Application Process Title given to the ICCP application instance. Note that the assignments follow the standard notation defined in the NICD as individual parameters. The format for entry of the AP Title in your system will depend on your vendor’s configuration user interface. | 1 2 30 33 | 2 16 1 XX XX XX XX 49 73 | 2 16 1 XX XX XX XX 50 73 |
| AE Qualifier: This parameter is required on some ICCP implementations if ICCP is communicating with multiple clients and/or servers. Refer to your vendor documentation to determine if a value is required. | 1 | 1 | 1 |
| AP InvokeID: | 100 | 100 | 100 |
| AE InvokeID: | 1 | 1 | 1 |
| Presentation Selector (PSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 00 00 33 | 00 00 00 01 | 00 00 00 01 |
| Session Selector (SSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 33 | 00 01 | 00 01 |
| Transport Selector (TSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 33 | 00 01 | 00 01 |

## QSE ICCP Data Exchange Requirements

### QSE ICCP Object Naming Convention

Two ICCP Object naming conventions are defined in this section. The first convention described in Section 4.4.1.1 applies to the exchange of generation and regulation signals. That is, the values sent to QSEs for generation and regulation, and the values received from QSEs declaring their performance capabilities and real-time response to ERCOT signals. The second naming convention described in Section 4.4.1.2 is identical to the naming convention used for TSP data. The values following the second convention apply to measured values and status indications from typical power system measuring devices, but that are unique to QSEs. For example, generator output values come from QSEs but not from TSPs. Although these values are certainly related to Resources, they are called non-generation values here simply to distinguish them from the specialized values used to exchange generation and regulation data with QSEs.

#### Object Names for Generation and Regulation

The ERCOT convention for generation and regulation ICCP Object names exchanged with QSEs is illustrated in the following name descriptor.

cccctttsssssssseeeeeeeedddduuuu

Where:

cccc	is the 4-character company name

ttt	is the 3-character equipment type descriptor

ssssssss	is the 8-character station name

eeeeeeee	is the 8-character equipment name

dddd	is an 8-character data descriptor

uuuu	is the 4-character unit of measure

Table 22 ICCP Object Names for Generation and Regulation Data Sent to QSEs

| Resource or Equipment Type | Type Descriptor | Data | Data Descriptor | Unit of Measure | ICCP Data Type | ICCP Object Name Example cccctttsssssssseeeeeeeedddduuuu |
| --- | --- | --- | --- | --- | --- | --- |
| Buss | BS | Locational Marginal Price | LMP | USD | RealQ | ACMQBS_GENSUB__BUSS1___LMP_USD_ |
| Load Zone | LZ | Locational Marginal Price | LMP | USD | RealQ | ACMQLZ_GENSUB__ZONE5___LMP_USD_ |
| Hub | HUB | Locational Marginal Price | LMP | USD | RealQ | ACMQHUBGENSUB__HUB3____LMP_USD_ |
| QSE | QSE | Regulation Down | REGD | MW | RealQ | ACMQQSEQSE_____QSE_____REGDMW__ |
|  |  | Regulation Up | REGU | MW | RealQ | ACMQQSEQSE_____QSE_____REGUMW__ |
|  |  | Emergency Dispatch on/off | EMBP | ST | StateQ | ACMQQSEQSE_____QSE_____EMBPST |
|  |  | Responsive Reserve | RR | MW | RealQ | ACMQQSEQSE_____QSE_____RR__MW__ |
| Controllable Load Resource | CLR | Base Point | BP | MW | RealQ | ACMQCLRSUBONE__LOAD1___BP__MW__ |
|  |  | Time of Dispatch | BP | TIM | RealQ | ACMQCLRSUBONE__LOAD1___BP__TIM_ |
|  |  | Desired Generation | GEN | MW | RealQ | ACMQCLRSUBONE__LOAD1___GEN_MW__ |
| Generation Unit | UN | Base Point | BP | MW | RealQ | ACMQUN_GENSUB__UNIT1___BP__MW__ |
|  |  | Time of Dispatch | BP | TIM | RealQ | ACMQUN_GENSUB__UNIT1___BP__TIM_ |
|  |  | Desired Generation | GEN | MW | RealQ | ACMQUN_GENSUB__UNIT1___GEN_MW__ |

Table 23 ICCP Object Names for Generation Data Received from QSEs

| Resource or Equipment Type | Type Descriptor | Data | Data Descriptor | Unit of Measure | ICCP Data Type | ICCP Object Name Example cccctttsssssssseeeeeeeedddduuuu |
| --- | --- | --- | --- | --- | --- | --- |
| Generation Unit | UN | Combine-cycle configuration number | CCC | INDX | DiscreteQ | ACMQUN_GENSUB__UNIT1___CCC_INDX |
|  |  | Dynamically scheduled resource. | DSR | ST | StateQ | ACMQUN_GENSUB__UNIT1___DSR_ST__ |
|  |  | Emergency ramp rate | EMRR | MW | RealQ | ACMQUN_GENSUB__UNIT1___EMRRMW__ |
|  |  | High emergency limit | HEL | MW | RealQ | ACMQUN_GENSUB__UNIT1___HEL_MW__ |
|  |  | Reason limit is outside the HEL specified in the registration system | HELT | INDX | DiscreteQ | ACMQUN_GENSUB__UNIT1___HELTINDX |
|  |  | High sustained limit | HSL | MW | RealQ | ACMQUN_GENSUB__UNIT1___HSL_MW__ |
|  |  | Reason limit is outside the HSL specified in the registration system | HSLT | INDX | DiscreteQ | ACMQUN_GENSUB__UNIT1___HSLTINDX |
|  |  | Lower block status | LBST | ST | StateQ | ACMQUN_GENSUB__UNIT1___LBSTST__ |
|  |  | Low emergency limit | LEL | MW | RealQ | ACMQUN_GENSUB__UNIT1___LEL_MW__ |
|  |  | Reason limit is outside the LEL specified in the registration system | LELT | INDX | DiscreteQ | ACMQUN_GENSUB__UNIT1___LELTINDX |
|  |  | Low sustained limit | LSL | MW | RealQ | ACMQUN_GENSUB__UNIT1___LSL_MW__ |
|  |  | Reason limit is outside the LSL specified in the registration system | LSLT | INDX | DiscreteQ | ACMQUN_GENSUB__UNIT1___LSLTINDX |
|  |  | Normal ramp rate | NMRR | MW | RealQ | ACMQUN_GENSUB__UNIT1___NMRRMW__ |
|  |  | Non-spin responsibility | NSRS | MW | RealQ | ACMQUN_GENSUB__UNIT1___NSRSMW__ |
|  |  | Non-spin schedule | NSSC | MW | RealQ | ACMQUN_GENSUB__UNIT1___NSSCMW__ |
|  |  | Raise block status | RBST | ST | StateQ | ACMQUN_GENSUB__UNIT1___RBSTST__ |
|  |  | Regulation Down participation factor | RDPF | MW | RealQ | ACMQUN_GENSUB__UNIT1___RDPFMW__ |
|  |  | Regulation down responsibility | RDRS | MW | RealQ | ACMQUN_GENSUB__UNIT1___RDRSMW__ |
|  |  | Regulation down schedule | RDSC | MW | RealQ | ACMQUN_GENSUB__UNIT1___RDSCMW__ |
|  |  | Responsive reserve responsibility | RRRS | MW | RealQ | ACMQUN_GENSUB__UNIT1___RRRSMW__ |
|  |  | Responsive reserve schedule | RRSC | MW | RealQ | ACMQUN_GENSUB__UNIT1___RRSCMW__ |
|  |  | Generation resource status | RST | INDX | DiscreteQ | ACMQUN_GENSUB__UNIT1___RST_INDX |
|  |  | Reason ramp rate deviated from standard curve | RTXT | INDX | DiscreteQ | ACMQUN_GENSUB__UNIT1___RTXTINDX |
|  |  | Regulation Up participation factor | RUPF | MW | RealQ | ACMQUN_GENSUB__UNIT1___RUPFMW__ |
|  |  | Regulation up responsibility | RURS | MW | RealQ | ACMQUN_GENSUB__UNIT1___RURSMW__ |
|  |  | Regulation up schedule | RUSC | MW | RealQ | ACMQUN_GENSUB__UNIT1___RUSCMW__ |
| Controllable Load Resource | CLR | Emergency Ramp Rate | EMRR | MW | RealQ | ACLQCLRSUBONE__LOAD1___EMRRMW__ |
|  |  | High Emergency Limit | HEL | MW | RealQ | ACLQCLRSUBONE__LOAD1___HEL_MW__ |
|  |  | High Sustained Limit | HSL | MW | RealQ | ACLQCLRSUBONE__LOAD1___HSL_MW__ |
|  |  | Lower block status | LBST | ST | RealQ | ACLQCLRSUBONE__LOAD1___LBSTST__ |
|  |  | Low emergency limit | LEL | MW | RealQ | ACLQCLRSUBONE__LOAD1___LEL_MW__ |
|  |  | Low sustained limit | LSL | MW | RealQ | ACLQCLRSUBONE__LOAD1___LSL_MW__ |
|  |  | normal ramp rate | NMRR | MW | RealQ | ACLQCLRSUBONE__LOAD1___NMRRMW__ |
|  |  | Non-spin responsibility | NSRS | MW | RealQ | ACLQCLRSUBONE__LOAD1___NSRSMW__ |
|  |  | Non-spin schedule | NSSC | MW | RealQ | ACLQCLRSUBONE__LOAD1___NSSCMW__ |
|  |  | Raise block status | RBST | ST | StateQ | ACLQCLRSUBONE__LOAD1___RBSTST__ |
|  |  | Regulation Down participation factor | RDPF | MW | RealQ | ACLQCLRSUBONE__LOAD1___RDPFMW__ |
|  |  | Regulation down responsibility | RDRS | MW | RealQ | ACLQCLRSUBONE__LOAD1___RDRSMW__ |
|  |  | Regulation down schedule | RDSC | MW | RealQ | ACLQCLRSUBONE__LOAD1___RDSCMW__ |
|  |  | Responsive reserve responsibility | RRRS | MW | RealQ | ACLQCLRSUBONE__LOAD1___RRRSMW__ |
|  |  | Responsive reserve schedule | RRSC | MW | RealQ | ACLQCLRSUBONE__LOAD1___RRSCMW__ |
|  |  | Controllable Load Resource status | RST | ST | StateQ | ACLQCLRSUBONE__LOAD1___RST_ST__ |
|  |  | Regulation Up participation factor | RUPF | MW | RealQ | ACLQCLRSUBONE__LOAD1___RUPFMW__ |
|  |  | Regulation up responsibility | RURS | MW | RealQ | ACLQCLRSUBONE__LOAD1___RURSMW__ |
|  |  | Regulation up schedule | RUSC | MW | RealQ | ACLQCLRSUBONE__LOAD1___RUSCMW__ |
|  |  | Controllable Load Resource breaker status | LRCB | MW | StateQ | ACLQCLRSUBONE__LOAD1___LRCBMW__ |
|  |  | Scheduled Power Consumption | SPC | MW | RealQ | ACLQCLRSUBONE__LOAD1___SPC_MW__ |
|  |  | Load Resource Low Power Consumption | LPC | MW | RealQ | ACLQCLRSUBONE__LOAD1___LPC_MW__ |
|  |  | Load Resource Maximum Power Consumption | MPC | MW | RealQ | ACLQCLRSUBONE__LOAD1___MPC_MW__ |
| Non-Controllable Load Resource | LR | High-set under-frequency relay status | HSUF | MW | StateQ | ACLQLR_SUBONE__LOAD2___HSUFMW__ |
|  |  | Load Resource breaker status | LRCB | MW | StateQ | ACLQLR_SUBONE__LOAD2___LRCBMW__ |
|  |  | Load Resource status | RST | ST | StateQ | ACLQLR_SUBONE__LOAD2___RST_ST__ |
|  |  | Scheduled Power Consumption | SPC | MW | RealQ | ACLQLR_SUBONE__LOAD2___SPC_MW__ |
|  |  | Load Resource Low Power Consumption | LPC | MW | RealQ | ACLQLR_SUBONE__LOAD2___LPC_MW__ |
|  |  | Load Resource Maximum Power Consumption | MPC | MW | RealQ | ACLQLR_SUBONE__LOAD2___MPC_MW__ |
|  |  | Responsive reserve responsibility | RRRS | MW | RealQ | ACLQLR_SUBONE__LOAD2___RRRSMW__ |
|  |  | Responsive reserve schedule | RRSC | MW | RealQ | ACLQLR_SUBONE__LOAD2___RRSCMW__ |
|  |  | Non-spin responsibility | NSRS | MW | RealQ | ACLQLR_SUBONE__LOAD2___NSRSMW__ |
|  |  | Non-spin schedule | NSSC | MW | RealQ | ACLQLR_SUBONE__LOAD2___NSSCMW__ |

Note: Regarding the “text reasons”, NRG prefers to send to ERCOT the text reason(s) using API/XML.  If ICCP is definitely required, NRG would prefer using an indexed list of reasons, instead of using ICCP Block 4.

#### ICCP Object Names for Non-generation Data

The ERCOT convention for non-generation ICCP Object names exchanged with QSEs is illustrated in the following name descriptor. This convention is the same as the convention for TSPs.

cccctttssssssssvvvveeeeeeeeuuuu

Where:

cccc	is the 4-character company name

ttt	is the 3-character equipment type descriptor

ssssssss	is the 8-character station name

vvvv	is the 4-digit voltage level. The last digit of this name field is to the right of an implied decimal point. For example, if the voltage level is 138KV, then the digits 1380 would be entered. If the voltage level is 13.8KV, then the digits would be 0138.

eeeeeeee	is the 8-character equipment name

uuuu	is a 4-character units specification of the measured value

Each field in the name must be padded with underscores where necessary to meet the specified field component length. Underscores should not be used within a field component; although a dollar sign ($) can be used to separate parts of a name, use of no separators are preferred. Avoiding underscores ensures that a person reading the name can distinguish between a complete name and a field length filler character.

Table 24 ERCOT QSE Non-generation ICCP Data Object Naming Conventions

| Equipment Type | Type Descriptor | Measurement | Unit of Measure | ICCP Data Type | ICCP Object Name Example cccctttssssssssvvvveeeeeeeeuuuu |
| --- | --- | --- | --- | --- | --- |
| Controllable Load Resource | CLR | Megawatts | MW | RealQ | ACMQCLRSUBONE__0692LOAD1___MW__ |
|  |  | Megavars | MV | RealQ | ACMQCLRSUBONE__0693LOAD1___MV__ |
| Non-Controllable Load Resource | LR | Megawatts | MW | RealQ | ACMQLR_SUBONE__0690LOAD2___MW__ |
|  |  | Megavars | MV | RealQ | ACMQLR_SUBONE__0691LOAD2___MV__ |
| Generation Unit | UN | Megawatts | MW | RealQ | ACMQUN_GENSUB__0180GEN1____MW__ |
|  |  | Megavars | MV | RealQ | ACMQUN_GENSUB__0180GEN1____MV__ |
|  |  | Breaker status | ST | StateQ | ACMQUN_GENSUB__0180GEN1____ST__ |
| Weather Station | WS | Barometric Pressure | INCH | RealQ | ACMQWS_WNDSUB__0180BAROM1__INCH |
|  |  | Wind Direction | DEG | RealQ | ACMQWS_WNDSUB__0180ANAMOM1_DEG_ |
|  |  | Wind Speed | MPH | RealQ | ACMQWS_WNDSUB__0180ANAMOM1_MPH_ |
|  |  | Temperature | DEGC | RealQ | ACMQWS_WNDSUB__0180THERMO1_DEGC |

Note: what are the ICCP Data Object naming conventions for data listed in tables 30 and 31, as well as the Generator Step-up transformers tap position?

For both the above naming conventions, each field in the name must be padded with underscores where necessary to meet the specified field component length. Underscores should not be used within a field component; although a dollar sign ($) can be used to separate parts of a name, use of no separators are preferred. Avoiding underscores ensures that a person reading the name can distinguish between a complete name and a field length filler character.

QSEs may also provide data for equipment not monitored by TSPs but are required by ERCOT. The naming conventions for this data can be found in Section 5.4.1.

### QSE Transfer Set Definition Standards

There are three types of Transfer Sets within ICCP. Data exchange in the ERCOT system requires only the Data Set Transfer Set. A Transfer Set specifies the conditions under which a referenced Data Set is to be transferred from the server to the client. As a minimum, the QSE’s ICCP server shall support the following Transfer Set transmission parameters:

Start Time	Defines the time that the server is to begin monitoring conditions that will trigger a Data Set Information Report to be sent to the client.  In addition to a valid time value, a time value of zero shall be supported

Interval	Defines the frequency at which a periodic Data Set Information Report will be sent to the client.  This value shall be ignored unless Interval Timeout is specified as a Transmission Condition.  Limitations on the value of Interval can be.

Buffer Time	Defines the amount of time the server will wait after an object changes before generating the Data Set Information Report.  Buffer Time is applicable only to the Object Change Transmission Condition.

Integrity Check	Defines the frequency at which all of the objects in the Data Set will be sent to the client.  Integrity Check is applicable only if RBE is specified.  Limitations on the value of Integrity Check are the same as those for Interval and can be found in the Workbook.

RBE	Specifies whether the Data Set Information Report will contain all the objects in the Data Set or only the objects which have changed since the last Data Set Information Report.

The Transfer Set also includes a parameter that specifies the Transmission Condition.  That is, the condition(s) that the server must monitor once Start Time arrives.  As a minimum, the QSE’s ICCP server shall support the following Transmission Conditions:

Interval Timeout	This condition specifies that a Data Set Information Report shall be sent to the client each time Interval expires.

Object Change	This condition specifies that a Data Set Information Report shall be sent to the client whenever any object in the Data Set changes.

Integrity Timeout	This condition specifies that the entire Data Set is to be sent to the client in a Data Set Information Report whenever Integrity Check expires.

#### QSE Requirements for Generation Data

To receive generation and regulation signals from ERCOT, QSEs are required to use the Transfer Set parameters specified in Table 25. The QSE will acquire generation and regulation signals from ERCOT using two Data Sets that the QSE must create in the ERCOT QSE ICCP Servers. One Data Set will reference the data points produced for the QSE by ERCOT’s 5-minute Security Constrained Economic Dispatch (SCED) application; while the other Data Set will reference the regulation signals produced every 4-seconds by ERCOT’s Load Frequency Control (LFC) application. Each such Data Set must use the Transfer Set parameters specified in Table 25.

Table 25 QSE Generation Transfer Set Requirements

| Transfer Set Parameter | Value | Comments |
| --- | --- | --- |
| Start Time | Zero | Indicates that Start Time is Now. |
| Interval | n/a | Not used when the Transmission Condition is Object Change. |
| Buffer Time | 1 sec |  |
| Integrity Check | n/a | Integrity check is not applicable when RBE is false. |
| RBE | False | Causes all objects referenced in the related Data Set to be transferred when any object in the Data Set changes. |
| Interval Timeout | False |  |
| Object Change | True | Specifies that the Data Set Information Report be sent whenever an object in the Data Set changes. |
| Integrity Timeout | False |  |

These Transfer Set Parameters ensure that each new set of control signals produced by SCED and LFC will be transferred to the QSE. Furthermore, although SCED generally runs every 5-minutes, and LFC runs every 4-seconds, each production of a new value by either application will be transferred to the QSE client regardless of the application execution cycles.

The key components of Table 25 are the Object Change and RBE parameters. When Object Change is True and RBE is False, all values in the Data Set will be transferred to the QSE client when any value in the Data Set is changed.

#### QSE Requirements for Non-Generation Data

In its ICCP server role, ERCOT will be processing data requests from many Market Participants. In order to minimize the performance impact on the ERCOT system, non-generation related data received by QSEs shall adhere to the following Transfer Set and Data Set limitations:

- Status data shall always be acquired using Report by Exception. The Integrity Interval shall be 30 minutes or longer.

- Values representing analog measurements and counters shall be acquired at an interval of 30 seconds or longer.

- Data Sets shall not contain mixed data types that would cause a conflict in the Transfer Set limitations specified above. More specifically, Data Sets containing analog measurements and counters shall not also contain status values unless the status values therein are a direct component of the measurements or counters.

### Data Sent to QSEs

Table 26 - Per-QSE Data Sent to QSE

| Per-QSE Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Regulation Up MW | 4 | 6.5.7.6.2.1 (8) |
| Regulation Down MW | 4 | 6.5.7.6.2.1 (8) |
| Responsive Reserve MW | 4 | 6.5.7.6.2.2 (11) |
| Emergency Basepoint (on/off) | 4 | 6.5.9 (1) |

Table 27 - Per- Resource Data Sent to QSE

| Per-Generation Resource Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Updated Desired Generation | 4 | 6.5.7.6.1 (9) |
| Resource Base Point MW | 4 | 6.5.7.4 (1) b |
| Resource LMP | 4 | 6.3.2 (2) table |
| Time of Dispatch for Base Point | 4 | 6.5.7.4 (1) d |
| Other possible information (multiple values) for Base Point | 4 | 6.5.7.4 (1) e |

Table 28 - Per-Hub Data Sent to QSE

| Per-Bus Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Hub LMP | 4 | 6.3.2 (2) |

Table 29 - Per-Load Zone Data Sent to QSE

| Per-Bus Data Sent to QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Load zone LMP | 4 | 6.3.2 (2) |

### Data Received from QSEs

Table 30 - Per-QSE Data Received from QSE

| Per-QSE Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Frequency (system) | 2 | 6.5.7.6.1 (3) |
| Any agreed-upon additional data Resource (multiple data items) | various | 6.5.5.2 (2) e 6.5.5.2 (4) b |

Table 31 - Per-Plant Data Received from QSE

| Per-Plant Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Power to standby transformers serving Plant auxiliary Load (MW) | 10 | 6.5.5.2 (2) c |
| Switch status not monitored by TSP (possibly multiple switches) | 10 | 6.5.5.2 (2) d |

Table 32 - Per-Generation Resource Data Received from QSE

| Per-Generation Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Combined Cycle config no. | 2 | 6.5.5.2 (8) b |
| Resource Status | 2 | 6.4.5 (1) 6.5.5.1 (1) |
| Generation Resource Net MW (to be used in LFC and SCED) | 2 | 6.5.5.2 (2) a |
| Generation Resource MVAR | 2 | 6.5.5.2 (2) b |
| Generation Resource Breaker status | 2 | 6.5.5.2 (2) f |
| Generation Resource High Sustained Limit (HSL) and Text Reason why limit is less than that limit specified in the Registration system | 2 | 6.4.5 (1) 6.5.5.2 (2) g 6.5.7.1.13 (1) (d) (ii) (B) |
| Generation Resource Low Sustained Limit (LSL) and Text Reason why limit is less than that limit specified in the Registration system | 2 | 6.4.5 (1) 6.5.5.2 (2) j 6.5.7.1.13 (1) (d) (ii) (C) |
| Generation Resource High Emergency Limit (HEL) and Text Reason why limit is less than that limit specified in the Registration system) | 2 | 6.5.5.2 (2) h |
| Generation Resource Low Emergency Limit (LEL) and Text Reason why limit is less than that limit specified in the Registration system | 2 | 6.5.5.2 (2) i |
| Text reason for any Resource where actual Ramp Rate is deviating from the Ramp Rate curve for the Resource. | 10 | 6.4.5 (1) |
| Generation Resource Reg-Up Ancillary Service Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource Reg-Down Ancillary Service Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource Responsive Reserve Ancillary Service Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource Non-Spin Ancillary Service Schedule | 2 | 6.5.5.2 (2) k |
| Generation Resource Reg-Up participation factor | 2 | 6.5.5.2 (2) l |
| Generation Resource Reg-Down participation factor | 2 | 6.5.5.2 (2) l |
| Generator Reg-Up Ancillary Service Resource Responsibility | 2 | whitepaper |
| Generator Reg-Down Ancillary Service Resource Responsibility | 2 | whitepaper |
| Generator Responsive Reserve Ancillary Service Resource Responsibility | 2 | whitepaper |
| Generator Non-Spin Ancillary Service Resource Responsibility | 2 | whitepaper |
| Generation Resource Raise block status | 2 | 6.5.5.2 (6) |
| Generation Resource Lower block status | 2 | 6.5.5.2 (6) |
| Generation Resource Normal Ramp Rate | 2 | 6.4.5 (1) |
| Generation Resource Emergency Ramp Rate | 2 | 6.4.5 (1) |
| Generation Resource DSR Schedule | 2 | 6.5.7.6.1 (8) j |
| Generator Step-up transformers tap position | 10 | 6.5.7.1.13 (1) (d) (ii) (A) |

Table 33 - Per-Load Resource Data Received from QSE

| Per-Load Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Load Resource MW | 2 | 6.5.5.2 (4) a |
| Resource Status | 2 | 6.4.5 (1) 6.5.5.1 (1) 6.5.5.2 (8) b 6.5.5.2 (8) c |
| Load Resource breaker status | 2 | 6.5.5.2 (4) c |
| High-set under-frequency relay status (if required for qualification) | 2 | 6.5.5.2 (4) g |
| Scheduled Power Consumption | 2 | 6.5.5.2(4) h |
| Net Reactive Power | 2 | 6.5.5.2 (4) i |
| Load Resource Low Power Consumption (LPC) | 2 | 6.5.5.2 (4) d |
| Load Resource Maximum Power Consumption (MPC) | 2 | 6.5.5.2 (4) e |
| Controllable Load Resource High Sustained Limit | 2 |  |
| Controllable Load Resource Low Sustained Limit | 2 |  |
| Controllable Load Resource High Emergency Limit | 2 |  |
| Controllable Load Resource High Emergency Limit | 2 |  |
| Controllable Load Resource Reg-Up Ancillary Service Schedule | 2 | 3.6 (implied) |
| Controllable Load Resource Reg-Down Ancillary Service Schedule | 2 | 3.6 (implied) |
| Load Resource Responsive Reserve Ancillary Service Schedule | 2 | 6.5.5.2 (4) f |
| Load Resource Non-Spin Ancillary Service Schedule | 2 | 3.6 (implied) |
| Controllable Load Resource Reg-Up participation factor | 2 | 3.6 (implied) |
| Controllable Load Resource Reg-Down participation factor | 2 | 3.6 (implied) |
| Load Resource Reg-Up Ancillary Service Resource Responsibility | 2 | whitepaper |
| Load Resource Reg-Down Ancillary Service Resource Responsibility | 2 | whitepaper |
| Load Resource Responsive Reserve Ancillary Service Resource Responsibility | 2 | whitepaper |
| Load Resource Non-Spin Ancillary Service Resource Responsibility | 2 | whitepaper |
| Controllable Load Resource Raise block status | 2 | 6.5.5.2 (6) 3.6 (implied) |
| Controllable Load Resource Lower block status | 2 | 6.5.5.2 (6) 3.6 (implied) |
| Load Resource Normal Ramp Rate | 2 | 3.6 (implied) |
| Load Resource Emergency Ramp Rate | 2 | 3.6 (implied) |

Table 34 - Per Wind Resource Data Received from QSE

| Per Wind Resource Data Received from QSE | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Wind Speed | 10 | 6.5.7.1.13 (1) (e) 4.2.2 (1) (implied) |
| Wind Direction | 10 | 4.2.2 (1) (implied) |
| Temperature | 10 | 4.2.2 (1) (implied) |
| Barometric Pressure | 10 | 4.2.2 (1) (implied) |

# TSP Connection Requirements

## TSP Communication Requirements

Any TSP facility, whether primary or backup, involved in the transfer of the data identified in Section 5.4.3 and Section 5.4.4 is required to connect directly to the ERCOT Frame Relay and DACS Networks. If a TSP and QSE share the same EMS at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TSP and QSE share a centralized PBX, separate OPX circuits will be terminated for each Market Participant.  The Hotline is required for each Market Participant and will not be allowed to connect through the PBX.

Telemetry performance measures required by the protocols will always measure the performance of the entity responsible for the data as established in the protocols. Each entity using others to transfer their data to or from ERCOT must be responsible for the performance of that data regardless of the path the data takes to get to ERCOT.  Likewise, scan rate requirements in the protocols measure the data update requirement from the field device to ERCOT with no allowance for delays of shared data paths.

A TSP involved in the transfer of the data defined in Section 5.4.3 and Section 5.4.4 is required to provide the following communication resources to support the connection to the ERCOT private network:

- Provide an analog business phone line or PBX analog extension for trouble-shooting and maintenance of equipment.

- Provide a height of 24” of rack space in a 19” wide rack.

- Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above.

- Provide building wiring from circuit termination to equipment rack.

- Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility.

- Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors.

- Provide on site personnel to escort ERCOT employees or contractors.

- Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN.

- Market Participant will be required to sign a security connection agreement with ERCOT.

- Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site. Market Participants are responsible for their own security through this connection.

- Provide a channel bank with at least one T1 interface, 1 ringing generator, and 4 FXS. Connect FXS (e.g. PBX, key system) to the appropriate equipment.  On the digital T1 stream, levels for voice are zero dpm for transmit and receive and levels.

- Hotline must be a 500 set not attached to the Market Participant’s Phone System.

- Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended.

- Provide ERCOT internal IP addressing scheme for network design. This will be kept confidential.

## TSP Implementation Procedures

TSPs participating in the Texas Nodal Market, and are required to use the ERCOT private network for exchanging data with ERCOT, as defined in Section 5.4, must complete and submit the following documents to ERCOT:

Attachment A ERCOT WAN Connection Agreement

Attachment B Market Participant WAN Circuit Installation Site Survey

Attachment C Market Participant WAN Equipment Installation Site Survey

Market Participants participating in the Texas Nodal Market and are requesting to use the private network as an optional connection for exchanging data with ERCOT must complete and submit to ERCOT the above listed attachments, plus:

Attachment D ERCOT WAN Requirement Pricing Survey

TSPs must complete Circuit and Equipment Site Surveys for each site that ERCOT will connect to.

ERCOT will perform circuit and equipment installation at TSP sites in coordination with the TSP. TSPs should plan for adequate time for ERCOT’s procurement, installation, and testing of communication equipment.

Although you may fax or e-mail the required documents, you must also submit all original documentation to:

ERCOT
		Attn: Ted Hailu, Client Relations Manager
		2705 West Lake Drive
		Taylor, Texas 76574
		Phone: (512) 248-3873
		Fax: (512) 248-3886
		thailu@ercot.com

Revise above contact information to be current with the Texas Nodal Market point of contact.

## TSP Association Information Exchange Form (AIEF)

Electric Reliability Council of Texas

Association Information Exchange Form (AIEF)

| Date Completed by Market Participant: |  |
| --- | --- |
| Market Participant Company Name: |  |
| Contact Name: |  |
| Mailing Address: |  |
| City, State, Zip: |  |
| Phone: |  |
| Email: |  |

| ERCOT Name: | Electric Reliability Council of Texas |
| --- | --- |
| Contact Name: |  |
| Mailing Address: | 2705 West Lake Drive |
| City, State, Zip: | Taylor, Texas 76574 |
| Phone: |  |
| Email: |  |

Version: 0.01

Instructions

This form is used to exchange the information needed by ERCOT and you, the Market Participant, for configuring ICCP nodes. The form is designed for electronic transmittal (via email). ERCOT sends this form to you in response to your request for a connection.

You request a connection by filling out Attachments A, B, C, and D submitting them to ERCOT.

The AIEF consists of four forms, at least two of which must be completed. The forms are:

| Network Information Form | This form provides information applicable to all ICCP nodes. It includes platform identification, Domain and Bilateral Table names and Association type. This form must be completed. |
| --- | --- |
| Primary Site ICCP Node Form | This form provides information specific to the primary and backup ICCP nodes located at your primary operating site. Most of the information on this form provides addressing information. This form must be completed. If you have a third ICCP node at the primary site, identify it on the Secondary Site ICCP node Form. It will be evident by the information you provided in your Site Surveys that the third node is located at this site. |
| Secondary Site ICCP Node Form | This form provides information specific to the primary and backup ICCP nodes located at your secondary operating site. This form contains the same information fields as the Primary Site ICCP Node Form. You may refer to this site as your backup or disaster recovery site. We use the term “secondary site” to avoid confusion with the backup ICCP node. This form must be completed if you are installing ICCP nodes at a secondary site. If you have a development or training system at a secondary site that you wish to use as an operational backup (and no other backup site), then this ICCP node is considered by ERCOT to be your secondary site node. |
| Alternate Site ICCP Node Form | This form provides information specific to one or more ICCP nodes that may be located at a third facility. Some Market Participants may have a development or training system not located at the primary or secondary sites, but in addition to them, that they might use as a third level of backup. ERCOT does not maintain such a site. Note that if your development or training system will not be used as an operational backup, do not identify it on this form. Such ICCP nodes do not need to be known by ERCOT. |

Most of the information on the AIEF is defined by ERCOT on the basis of the Site Survey information you provided with your Connection Agreement. ERCOT sets up the addresses and other parameters required to complete the connection, then sends the AIEF to you. The information provided by ERCOT is shown in the fields shaded in light gray. You complete the unshaded fields and return the form to ERCOT.

Once ERCOT receives your completed AIEF, ERCOT will configure its ICCP nodes to communicate with yours. However, the links will remain turned off (disabled) until you communicate your readiness to perform the Certification Tests.

The AIEF cover page contains fields for you to enter your contact information. This information should apply to the person in your company who will be working with ERCOT to configure the ICCP nodes and validate the connection. Instructions for completing each of the form fields are given in the forms.

Table 35 TSP Network-wide Information Form

| Form Entry Description | ERCOT | Market Participant |
| --- | --- | --- |
| ICCP Vendor: | Areva |  |
| Vendor Software Version: | e-terracomm ver 2.4 |  |
| ICCP Server Hardware Platform: | IBM |  |
| ICCP Server Operating System: | Windows 2003 Server |  |
| Domain Name: The Domain name which each company’s client will use to access the other company’s server. For example, the domain name listed for ERCOT is the name that the Market Participant’s client will use to access ERCOT’s ICCP server. Conversely, the Domain name shown in the Market Participant column, is the Domain name the Market Participant must assign to ERCOT’s domain in the Market Participant’s ICCP server. | ERCT_XXXX_ISO | XXXX_ERCT_QSE |
| Association Type: Specify either “Single” or “Dual”. If the Market Participant’s ICCP product is capable of Dual use associations, then “Dual” must be specified and configured. Enter “Single” in the Market Participant’s column only if Dual cannot be supported. ERCOT will configure its ICCP nodes to match the specification you enter here. Therefore you can assume that ERCOT has placed the same specification in the ERCOT column. ERCOT will be the initiator when the Association type is specified as “Dual”. |  | Dual |
| Initial Bilateral Table Name: This is the assigned Bilateral Table Name according to the ERCOT naming standard, including the Bilateral Table Version number. | ERCT_XXXX_0001 | ERCT_XXXX_0001 |

Table 36 TSP Taylor Site ICCP Node Form

| Form Entry Description | ERCOT Primary ICCP Node | ERCOT Backup ICCP Node | Market Participant Primary ICCP Node | Market Participant Backup ICCP Node |
| --- | --- | --- | --- | --- |
| ICCP Node Name: The name by which people refer to this Node. This name is not transmitted during any ICCP transactions, but is only used to facilitate verbal communication between company personnel. | ERPICCPTA | ERPICCPTB | Filled in by Market Participant | Filled in by Market Participant |
| ICCP Node IP Address: This is the IP address assigned by ERCOT to access the ICCP node on the company internal LAN. The Market Participant may assign this IP address directly to the applicable ICCP node, or use Network Address Translation in a Market Participant-provided router or firewall. | xxx.xxx.xxx.xxx | xxx.xxx.xxx.xxx | mapped to xxx.xxx.xxx.xxx | mapped to xxx.xxx.xxx.xxx |
| AP Title: The Application Process Title given to the ICCP application instance. Note that the assignments follow the standard notation defined in the NICD as individual parameters. The format for entry of the AP Title in your system will depend on your vendor’s configuration user interface. | 2 16 1 69 82 67 84 49 73 | 2 16 1 69 82 67 84 50 73 | 2 16 1 XX XX XX XX 49 73 | 2 16 1 XX XX XX XX 50 73 |
| AE Qualifier: This parameter is required on some ICCP implementations if ICCP is communicating with multiple clients and/or servers. Refer to your vendor documentation to determine if a value is required. | 1 | 1 | 1 | 1 |
| Presentation Selector (PSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 |
| Session Selector (SSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |
| Transport Selector (TSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |

Table 37 TSP Austin Site ICCP Node Information

| Form Entry Description | ERCOT Primary ICCP Node | ERCOT Backup ICCP Node | Market Participant Primary ICCP Node | Market Participant Backup ICCP Node |
| --- | --- | --- | --- | --- |
| ICCP Node Name: The name by which people refer to this Node. This name is not transmitted during any ICCP transactions, but is only used to facilitate verbal communication between company personnel. | ERPICCPTC | ERPICCPTD | Filled in by Market Participant | Filled in by Market Participant |
| ICCP Node IP Address: This is the IP address assigned by ERCOT to access the ICCP node on the company internal LAN. The Market Participant may assign this IP address directly to the applicable ICCP node, or use Network Address Translation in a Market Participant-provided router or firewall. | xxx.xxx.xxx.xxx | xxx.xxx.xxx.xxx | mapped to xxx.xxx.xxx.xxx | mapped to xxx.xxx.xxx.xxx |
| AP Title: The Application Process Title given to the ICCP application instance. Note that the assignments follow the standard notation defined in the NICD as individual parameters. The format for entry of the AP Title in your system will depend on your vendor’s configuration user interface. | 2 16 1 69 82 67 84 51 73 | 2 16 1 69 82 67 84 52 73 | 2 16 1 XX XX XX XX 49 73 | 2 16 1 XX XX XX XX 50 73 |
| AE Qualifier: This parameter is required on some ICCP implementations if ICCP is communicating with multiple clients and/or servers. Refer to your vendor documentation to determine if a value is required. | 1 | 1 | 1 | 1 |
| Presentation Selector (PSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 |
| Session Selector (SSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |
| Transport Selector (TSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |

Table 38 TSP Test ICCP Node Information

| Form Entry Description | ERCOT Primary ICCP Node | ERCOT Backup ICCP Node | Market Participant Primary ICCP Node | Market Participant Backup ICCP Node |
| --- | --- | --- | --- | --- |
| ICCP Node Name: The name by which people refer to this Node. This name is not transmitted during any ICCP transactions, but is only used to facilitate verbal communication between company personnel. | ERTICCPTA | ERTICCPTB | Filled in by Market Participant | Filled in by Market Participant |
| ICCP Node IP Address: This is the IP address assigned by ERCOT to access the ICCP node on the company internal LAN. The Market Participant may assign this IP address directly to the applicable ICCP node, or use Network Address Translation in a Market Participant-provided router or firewall. | xxx.xxx.xxx.xxx | xxx.xxx.xxx.xxx | mapped to xxx.xxx.xxx.xxx | mapped to xxx.xxx.xxx.xxx |
| AP Title: The Application Process Title given to the ICCP application instance. Note that the assignments follow the standard notation defined in the NICD as individual parameters. The format for entry of the AP Title in your system will depend on your vendor’s configuration user interface. | 2 16 1 69 82 67 84 53 73 | 2 16 1 69 82 67 84 54 73 | 2 16 1 XX XX XX XX 49 73 | 2 16 1 XX XX XX XX 50 73 |
| AE Qualifier: This parameter is required on some ICCP implementations if ICCP is communicating with multiple clients and/or servers. Refer to your vendor documentation to determine if a value is required. | 1 | 1 | 1 | 1 |
| Presentation Selector (PSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 | 00 00 00 01 |
| Session Selector (SSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |
| Transport Selector (TSEL): A 2-byte or 4-byte number used to select the correct instance of the session layer (e.g. 00 09 or 00 00 00 09) | 00 01 | 00 01 | 00 01 | 00 01 |

## TSP ICCP Data Exchange Requirements

### ERCOT TSP ICCP Object Naming Convention

The ERCOT convention for ICCP Object names exchanged with TSPs is illustrated in the following name descriptor.

cccctttssssssssvvvveeeeeeeeuuuu

Where:

cccc	is the 4-character company name

ttt	is the 3-character equipment type descriptor

ssssssss	is the 8-character station name

vvvv	is the 4-digit voltage level. The last digit of this name field is to the right of an implied decimal point. For example, if the voltage level is 138KV, then the digits 1380 would be entered. If the voltage level is 13.8KV, then the digits would be 0138.

eeeeeeee	is the 8-character equipment name

uuuu	is a 4-character units specification of the measured value

Each field in the name must be padded with underscores where necessary to meet the specified field component length. Underscores should not be used within a field component; although a dollar sign ($) can be used to separate parts of a name, use of no separators are preferred. Avoiding underscores ensures that a person reading the name can distinguish between a complete name and a field length filler character.

Table 39 lists the types of data objects exchanged with TSPs and the labeling conventions for each.

Table 39 ERCOT TSP ICCP Data Object Naming Conventions

| Device | Type Descriptor | Measurement | Unit | ICCP Data Type | ICCP Object Name Example cccctttssssssssvvvveeeeeeeeuuuu |
| --- | --- | --- | --- | --- | --- |
| Bus | BS | Voltage | KV | RealQTimeTag | ACMEBS_EXASUB__3450BUS1A___KV__ |
|  |  | Frequency | HZ | RealQTimeTag | ACMEBS_EXASUB__3450BUS1A___KV__ |
| Transformer | XF | Megawatts | MW | RealQTimeTag | ACMEXF_EXASUB__1380AUTO1___MW__ |
|  |  | Megavars | MV | RealQTimeTag | ACMEXF_EXASUB__1380AUTO1___TAP_ |
|  |  | Tap Position | TAP | RealQTimeTag | ACMEXF_EXASUB__1380AUTO1___TAP_ |
|  |  | Status | ST | StateQTimeTag | ACMEXF_EXASUB__1380AUTO1___ST__ |
| Line | LN | Megawatts | MW | RealQTimeTag | ACMELN_EXASUB__0690SBA$SBB1MW__ |
|  |  | Megavars | MV | RealQTimeTag | ACMELN_EXASUB__0690SBA$SBB1MV__ |
|  |  | Status | ST | StateQTimeTag | ACMELN_EXASUB__0690SBA$SBB1ST__ |
| Reactor | SH | Megavars | MV | RealQTimeTag | ACMESH_EXASUB__1380SHU1____MV__ |
|  |  | Megawatts | MW | RealQTimeTag | ACMESH_EXASUB__1380SHU1____MW__ |
|  |  | Status | ST | StateQTimeTag | ACMESH_EXASUB__1380SHU1____ST__ |
| Breaker | CB | Megawatts | MW | RealQTimeTag | ACMECB_EXASUB2_3450OCB3580_MW__ |
|  |  | Megavars | MV | RealQTimeTag | ACMECB_EXASUB2_3450OCB3580_MV__ |
|  |  | Status | ST | StateQTimeTag | ACMECB_EXASUB2_3450OCB3580_ST__ |
| Load | LD | Megawatts | MW | RealQTimeTag | ACMELD_EXASUB1_0690XLD1____MW__ |
|  |  | Megavars | MV | RealQTimeTag | ACMELD_EXASUB1_0690XLD1____MV__ |
| DC Injection | DC | Megawats | MW | RealQTimeTag | ACMEDC_DCTM-E__3450DC1_____MW__ |
|  |  | Status | ST | StateQTimeTag | ACMEDC_DCTM-E__3450DC1_____ST__ |
| Capacitor | CP | Megavars | MV | StateQTimeTag | ACMECP_EXASUB__1380CP1_____MV__ |
|  |  | Megawatts | MW | RealQTimeTag | ACMECP_EXASUB__1380CP1_____MW__ |
|  |  | Status | ST | StateQTimeTag | ACMECP_EXASUB__1380CP1_____ST__ |

Bit configurations for status indication and units of measure and sign conventions for measured quantities are specified in Section 3.5.

### TSP Transfer Set Definition Standards

There are three types of Transfer Sets within ICCP. Data exchange in the ERCOT system requires only the Data Set Transfer Set. A Transfer Set specifies the conditions under which a referenced Data Set is to be transferred from the server to the client. As a minimum, the TSP’s ICCP server shall support the following Transfer Set transmission parameters:

Start Time	Defines the time that the server is to begin monitoring conditions that will trigger a Data Set Information Report to be sent to the client.  In addition to a valid time value, a time value of zero shall be supported

Interval	Defines the frequency at which a periodic Data Set Information Report will be sent to the client.  This value shall be ignored unless Interval Timeout is specified as a Transmission Condition.  Limitations on the value of Interval can be.

Buffer Time	Defines the amount of time the server will wait after an object changes before generating the Data Set Information Report.  Buffer Time is applicable only to the Object Change Transmission Condition.

Integrity Check	Defines the frequency at which all of the objects in the Data Set will be sent to the client.  Integrity Check is applicable only if RBE is specified.  Limitations on the value of Integrity Check are the same as those for Interval and can be found in the Workbook.

RBE	Specifies whether the Data Set Information Report will contain all the objects in the Data Set or only the objects which have changed since the last Data Set Information Report.

The Transfer Set also includes a parameter that specifies the Transmission Condition.  That is, the condition(s) that the server must monitor once Start Time arrives.  As a minimum, the TSP’s ICCP server shall support the following Transmission Conditions:

Interval Timeout	This condition specifies that a Data Set Information Report shall be sent to the client each time Interval expires.

Object Change	This condition specifies that a Data Set Information Report shall be sent to the client whenever any object in the Data Set changes.

Integrity Timeout	This condition specifies that the entire Data Set is to be sent to the client in a Data Set Information Report whenever Integrity Check expires.

Data Sets and Transfer Sets are used to organize data into different timing groups and exception reporting groups.  In its ICCP server role, ERCOT will be processing data requests from many Market Participants. In order to minimize the performance impact on the ERCOT system, TSPs shall adhere to the following Transfer Set and Data Set limitations:

- Status data shall always be acquired using Report by Exception. The Integrity Interval shall be 30 minutes or longer.

- Values representing analog measurements and counters shall be acquired at an interval of 30 seconds or longer.

- Data Sets shall not contain mixed data types that would cause a conflict in the Transfer Set limitations specified above. More specifically, Data Sets containing analog measurements and counters shall not also contain status values unless the status values therein are a direct component of the measurements or counters.

Some of the required data exchange transactions specified in Section 5.4.3 and Section 5.4.4 exceed the restrictions given here. The timing specifications in the tables take precedence over these limitations. However, only the transactions defined in the tables are allowed to exceed these limitations.

### Data Received from TSPs

Table 40 - Per-Buss Data Received from TSP

| Per-Buss Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Buss Voltage kV | 10 | 6.5.7.1.13 (1) (a) (i) |

Table 41 - Per-Transformer Data Received from TSP

| Per-Transformer Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Transformer Flow MW | 10 | 6.5.7.1.13 (1) (a) (ii) |
| Transformer Flow MVAR | 10 | 6.5.7.1.13 (1) (a) (ii) |
| LTC Tap Position | 10 | 6.5.7.1.13 (1) (a) (v) |

Table 42 - Per-Transmission Line Data Received from TSP

| Per-Transmission Line Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Line Flow MW | 10 | 3.10.7.4.2 6.5.7.1.13 (1) (a) (ii) |
| Line Flow MVAR | 10 | 3.10.7.4.2 6.5.7.1.13 (1) (a) (ii) |

Table 43 - Per-Reactor (Inductive or Capacitive) Data Received from TSP

| Per-Reactor (Inductive or Capacitive) Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Reactor MVAR | 10 | 6.5.7.1.13 (1) (a) (ii) |

Table 44 - Per-Circuit Breaker Data Received from TSP

| Per-Circuit Breaker Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Breaker Status | 10 | 3.10.7.4.1 (1) 6.5.7.1.13 (1) (a) (iii) 6.5.7.1.13 (1) (a) (iv) |

Table 45 - Per-Load Data Received from TSP

| Per-Load Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Switch Status | 10 | 3.10.7.4.1 (1) 6.5.7.1.13 (1) (a) (iv) 6.5.7.1.13 (1) (a) (iii) |
| Load in MW | 10 | 3.10.7.4.2 (1) |
| Load in MVAR | 10 | 3.10.7.4.2 (1) |

Table 46 - Per-DC Injection Point Data Received from TSP

| Per-DC Injection Point Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| DC Injection in MW | 10 | 3.10.7.2 (3) |
| DC Injection in MVAR | 10 | 3.10.7.2 (3) |
| DC Tie Status | 10 | 3.10.7.2 (3) (implied) |

Table 47 - Per- Block Load Transfer Point Data Received from TSP

| Per-Block Load Transfer Point Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Switching Device Status at BLT points | 10 | 6.5.9.5 (i) |
| BLT MW | 10 | 6.5.9.5(i) |
| BLT MVAR | 10 | 6.5.9.5(i) |

Table 48 - Per Weather Zone Tie Line Data Received from TSP

| Per Weather Zone Tie Line Data Received from TSP | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Temperature | 10 | 6.5.7.1.13 (1) (e) 6.5.7.1.7 (1) |
| Wind Speed (if available) | 10 | 6.5.7.1.13 (1) (e) 6.5.7.1.7 (1) |

### Optional TSP Data Exchange

The data specified in the following tables included in this section may not be exchanged by all TSPs. For Dynamic Ratings, TSPs may alternatively provide ERCOT with a table of equipment ratings versus temperatures from which ERCOT will calculate ratings based on the temperature value provided in Table 48.

Table 49 - Per Dynamic Rating Data Received from TSP

| Per Dynamic Rating Data Received from TSP | Frequency (min) | Nodal Protocol Reference |
| --- | --- | --- |
| Line ID | 10 | 3.10.8.1 (1) (a) |
| From Station | 10 | 3.10.8.1 (1) (b) |
| To Station | 10 | 3.10.8.1 (1) (c) |
| Normal Rating | 10 | 3.10.8.1 (1) (d) |
| Emergency Rating | 10 | 3.10.8.1 (1) (d) |
| 15-Minute Rating | 10 | 3.10.8.1 (1) (d) |

# Data Available to All Market Participants

The data specified in Table 50 is provided in the SCADA database and is available to all Market Participants via ICCP. This data is also available to Market Participants in ERCOT’s MIS secure area which is a system separate from the EMS.

Table 50 - Data Available for Reading by All Market Participants

| Data Available for Reading by Market Participants | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Responsive Reserve Capacity from Generation Resources | 10 | 6.5.7.5 (1) a |
| Responsive Reserve Capacity from Load Resources excluding Controllable Load Resources | 10 | 6.5.7.5 (1) b |
| Responsive Reserve Capacty from Controllable Load Resources | 10 | 6.5.7.5 (1) c |
| Non-Spinning Reserve available from On-Line Generation Resources with Energy Offer Curves | 10 | 6.5.7.5 (1) d |
| Non-Spinning Reserve available from undeployed Load Resources | 10 | 6.5.7.5 (1) e |
| Non-Spinning Reserve available from Off-Line Generation Resources | 10 | 6.5.7.5 (1) f |
| Non-Spinning Reserve available from Resources with Output Schedules | 10 | 6.5.7.5 (1) g |
| Undeployed Reg-Up and undeployed Reg-Down | 10 | 6.5.7.5 (1) h |
| Available capacity with Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | 10 | 6.5.7.5 (1) i |
| Available capacity with Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | 10 | 6.5.7.5 (1) j |
| Available capacity without Energy Offer Curves in the ERCOT System that can be used to increase Base Points in SCED | 10 | 6.5.7.5 (1) k |
| Available capacity without Energy Offer Curves in the ERCOT System that can be used to decrease Base Points in SCED | 10 | 6.5.7.5 (1) l |
| Total ERCOT Load | 10 |  |
| Total ERCOT Generation | 10 |  |
| Total ERCOT Generation Operating Reserve | 10 |  |

# Data Calculated Locally by ERCOT

The data specified in the tables included in this section are calculated based on the respective MW/MVAR pair received from TSPs.

Table 51 - Per-Transformer Data

| Per-Transformer Data | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Transformer Flow MVA | 10 | 6.5.7.1.13 (1) (a) (ii) |

Table 52 - Per-Transmission Line Data

| Per-Transmission Line Data | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Line Flow MVA | 10 | 3.10.7.4.2 6.5.7.1.13 (1) (a) (ii) |
| Normal Rating for dynamically rated lines | 10 | 3.10.8.1 (1) (d) |
| Emergency Rating for dynamically rated lines | 10 | 3.10.8.1 (1) (d) |
| 15-Minute Rating for dynamically rated lines | 10 | 3.10.8.1 (1) (d) |

Table 53 - Per-Reactor (Inductive or Capacitive) Data

| Per-Reactor (Inductive or Capacitive) Data | Frequency (sec) | Nodal Protocol Reference |
| --- | --- | --- |
| Reactor Flow MVA | 10 | 6.5.7.1.13 (1) (a) (ii) |

##### ERCOT WAN Connection Agreement

THIS ATTACHMENT MUST BE REQUESTED FROM THE MARKET PARTICIPANT’S CLIENT REPRESENTATIVE

##### Market Participant WAN Circuit Installation Site Survey

Market Participants required to exchange critical data on the ERCOT private network must complete the following site survey.

Market Participants requesting an optional connection to ERCOT private network must also complete the following site survey.

Complete a separate site survey for each Market Participant location that will be connecting to the ERCOT private network.

WAN Circuit Installation Site Survey:

Market Participant:____________________________________________________________________

Address:

Street: ________________________________________________________________________

City: _________________________________	State: _________ Zip Code: ________________

Circuit Termination – 	Building: __________________________

Floor: _____________________________

Room: ____________________________

NPA-NXX Code:____________________

Points of Contacts:

Installation Contact (Primary) – 		Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Installation Contact (Back-Up) – 		Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Service Contact (Primary) – 		Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Service Contact (Back-up) – 		Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Management Contact – 			Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

24x7 Service Contact (After hours) –	Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

24x7 Real Time Operations Desk	Telephone: ____________________________________

Long Distance Phone Number

##### Market Participant WAN Equipment Installation Site Survey

Market Participants required to exchange critical data, as defined by Attachment A, on the ERCOT private network must complete the following site survey.

Market Participants requesting an optional connection to ERCOT private network must also complete the following site survey.

Complete a separate site survey for each Market Participant location that will be connecting to the ERCOT private network.

WAN Equipment Installation Site Survey:

Market Participant: ____________________________________________________________________

Address:

Street: ________________________________________________________________________

City: _________________________________	State: _________ Zip Code: ________________

Circuit Termination – 	Building: __________________________

Floor: _____________________________

Room: ____________________________

NPA-NXX Code:_____________________

Points of Contacts:

Installation Contact (Primary) – 		Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Installation Contact (Back-Up) –	 	Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Service Contact (Primary) – 		Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Service Contact (Back-up) – 		Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

Management Contact – 			Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

24x7 Service Contact (After hours) –	Name: ________________________________________

Telephone: ____________________________________

Email: ________________________________________

NON PBX #: ___________________________________

24x7 Real Time Operations Desk	Telephone: ____________________________________

Long Distance Phone Number

##### ERCOT WAN Requirement Pricing Survey

Market Participants requesting connection to the ERCOT private network must complete the following survey and submit back to ERCOT.  This information will be used by ERCOT to establish pricing for a potential service agreement with the Market Participants.

Market Participant (name of organization):

_________________________________________________________________________________

Installation Options (check one):

DACS Point to Point Circuit

(Voice Only)

Frame Relay Circuit Only

(Data Only, no circuit redundancy required)

Frame Relay Circuit and DACS Point to Point Circuit for data

(Provides a back-up data communications path to the Frame Relay Circuit)

Frame Relay Circuit and DACS Point to Point Circuit with additional OPX voice circuits directly to ERCOT (Provides a back-up data communications path to the Frame Relay Circuit and permits voice communications with ERCOT over the private network)

Technical Information (complete all blanks):

Required Bandwidth: ___________________________	(Kbps)

Frame Switch Port Speed: _______________________	(Kbps)

Private Virtual Circuit Speed: _____________________	(Kbps)

Point of Contact (complete all blanks):

Name: ____________________________________________

Telephone: ________________________________________

Email: ____________________________________________

- Index

Access Control, 22

AE Qualifier, 53, 55, 57, 78, 80, 82

AIEF, 20, 21, 23, 27, 49, 50, 51, 73, 74, 75

Defined, 9

AP Title, 19, 20, 21, 53, 55, 57, 77, 79, 81

Application Process Title. See AP Title

Association

Dual-use, 18

Single-use, 18

Association Information Exchange Form. See AIEF

Bilateral Agreement, 22, 23

Bilateral Table, 20, 22, 23, 50, 52, 74, 76

Identifier, 22

Name, 23

Version, 23, 52, 76

Company Identifier, 23, 25, 27

Connection Agreement, 15, 47, 71

CSU/DSU, 14

Current Provider, 10, 31, 32

Defined, 10

Current Source, 10, 31, 32, 33, 38, 39, 40, 41, 42, 43, 44

Defined, 10

Customer Premises Equipment, 14

DACS Network, 11, 13

Data Set, 24, 27, 28, 65, 66, 85, 86

Development System, 20

Domain Name, 25

EMS, 7, 10, 14, 17, 24, 47, 71, 89

Ethernet connections, 17

Frame Relay Network, 11, 13

Generation Data

Output Specification, 66

High Availability Data, 14

ICCP

Associations, 8, 9, 15, 17, 18, 19, 20, 21, 22, 23, 25, 49, 50, 52, 73, 74, 76

Associations Identifiers, 19

Client, 8, 17, 18, 19, 22, 23, 24, 25, 26, 27, 52, 65, 76, 85

Conformance Blocks, 7, 19, 22, 24

Defined, 10

Domain, 22, 23, 25, 26, 27, 50, 74

Domain Name, 20, 25, 26, 27, 52, 76

Node, 20, 50, 53, 55, 57, 74, 77, 79, 81

Server, 8, 14, 17, 18, 19, 22, 23, 24, 25, 26, 27, 28, 52, 65, 66, 76, 85

IP Address, 21, 53, 55, 57, 77, 79, 81

line of demarcation, 13, 17, 21

MMS PDU Size, 24

Network Address Translation (NAT), 21

Normal Provider, 31

Defined, 10

Normal Source, 31, 32, 39, 40

Defined, 10

Normal Value, 31, 38, 39, 40, 41, 42, 43, 44

Defined, 10

Permanent Virtual Circuit, 19

physical connections, 7

Physical layer, 7, 17

Physical Layer, 12

Presentation Selector (PSEL), 20, 53, 55, 57, 78, 80, 82

Protocol Selectors, 20

QSE, 8, 14, 15, 47, 67, 68, 69, 70, 76

Qualified Scheduling Entity. See QSE

RFC 1006, 20

Transport Mapping Layer, 17

Session Selector (SSEL), 20, 54, 56, 57, 78, 80, 82

Switch, 14

TASE.2 Version, 22

TCP Port Number usage, 20

TCP/IP, 7, 11, 17

Transfer Set, 24, 65, 66, 85, 86

Transmission Service Provider. See TSP

Transport, 20

Transport Layer Service Access Point (TSAP), 20

Transport Selector (TSEL), 20, 54, 56, 58, 78, 80, 82

TSP, 8, 14, 15, 47, 68, 71, 86, 87

WAN, 8, 11, 15, 95, 99

Wide Area Network. See WAN

For information such as schedules, forecasts, and other similar data, ERCOT provides the Portal and API (Programmatic Interface [PI]) interfaces. Refer to the guides for these interfaces as well as the ERCOT XML specifications for more information.

TCP does not communicate with ICCP. Rather, it communicates with the ISO Transport service. The higher layers of the protocol stack then identify ICCP by the AP Title described in Section 3.1.3.

In order to ensure the best possible performance from the ERCOT Private Network, ERCOT has designed an IP addressing plan supporting efficient routing updates. Specifically, ERCOT makes extensive use of subnetting to minimize traffic generated by the routing protocols (routing table updates). Participants also need the flexibility to implement their own addressing plans for the same reason. Implementing NAT allows both organizations to meet their performance requirements with a minimum of conflicts.

This is the function of the ICCP service called GetDataValueNames. The availability of a tool to access the data object list is product dependent. Participant’s should ask their vendors if such a tool is available.

If the Market Participant implements a single ICCP server to exchange data for both QSE services and TSP services, then two domains would be created in the Market Participant’s server, one named ACME_ERCT_NTSP, and one named ACME_ERCT_NQSE.

This naming convention for Data Sets is a recommendation only.  Some implementations create Data Set names internally so that the user has no control over their form.  For those systems where the user can assign Data Set names, the convention specified here is the preferred form.

ERCOT ignores the ICCP attribute Normal Source. The normal source of a point is established by the bilateral agreement between ERCOT and the Market Participant, and is recorded locally in the ERCOT SCADA database.