April 24, 2007

Bob Green, Garland Power & Light

RE: ERCOT Nodal ICCP Handbook

General Comments

- Can Time of Dispatch (Table 22) be sent in RealQ format?

- Table 22 does not have Resource LMP.

- Are you sure you want RegDn Schedule and RegUp Schedule in Tables 23 and 32?  I thought these deployments were so transient that we did not want to them to change HASL and LASL in real-time.

- DSR Status (second item in Table 23) for each Resource seems to be something new.  What is the definition of this variable?

- I could not find a table that showed the number (index) that needs to be sent for each of the Resource Status (Table 23).

- Thanks for adding Non-CLR Load Resources to Tables 23 and 24.  Can the same information be added following Table 34?

- Section 4.4.1.2 (and Table 24) includes generation data, so the section heading might need to be changed or data moved to Table 23.

- I don’t think there will be a QSE level Non-Spin (deployment) sent to the QSE as shown in Table 26.

- I thought that generator step up transformer tap (Table 32) was deleted from a previous revision to the SCADA Requirement document.  These are normally only changed seasonally when the unit is off-line.

- DSR Load is not shown in Table 30.

- There are no object names for Frequency and DSR Load in Table 24 (QSE to ERCOT).