## Slide 1: Tuning Changes 3/26/07 – 4/30/07
SCE feedback disabled
Assist from 156MW to 161MW (30mHz to 31mHz)
Emergency Assist from 260MW to 239MW (50mHz to 46mHz)
Normal gain from 0.3 to 0.3 (many changes)
Assist gain from 0.52 to 0.46
Static deadband from 56MW to 48MW
Stall boost from 50 MW to 40 MW
Non-Conforming Load was briefly used

## Slide 2
Received positive feedback from QSEs at PDCWG meeting (fewer unit reversals)
CPS1 monthly score improved from 120.59 in March to 126.92 in April
CPS2 monthly score improved from 86.43 in March to 88.08 in April
Results of Tuning

## Slide 3
Problems with further Improvement
  All settings are based on ERCOT ACE. Turbine governor deadbands are set based on 60.00 Hz. When ERCOT performs Time Error corrections, the ACE scheduled frequency is offset by +/- 0.02 Hz. This causes the thresholds of the Assist and Emergency Assist of the Regulation deployment to NOT be coordinated with the governor dead-bands. This will result in poorer control during Time Error corrections. This is not a new problem.

## Slide 4
ESCA Frequency Control “Persistence” logic is not fully understood. Some Regulation deployment “stall” continues to delay deployment sooner than needed. Further investigation into the logic may improve this.
ERCOT Frequency Desk Operator has, for the most part, left the “Requested ACE % Feedback” set at 100 for the past month.
Problems with further Improvement
(continued)

## Slide 6
Red Bar – Regulation Provider