## Slide 1: Compliance Update
May 2007

## Slide 2: Control Performance Highlights
NERC CPS1 Performance
  Performance further declined in March
    March performance comparison
      March 2007: 120.59
      March 2006: 143.16
    12 month rolling average comparison
      April 2006 March 2007: 139.59
      April 2005 March 2006: 128.56
PRR 525 Performance
  Scores for March indicate 32 QSEs passed / 3 non-wind-only QSEs failed the measure
  Scores posted on the ERCOT Compliance Website
    SCE Performance Scores

## Slide 3: ERCOT CPS1 Performance Comparison

## Slide 4: ERCOT’s CPS1 Monthly Trend

## Slide 5: ERCOT CPS1 by Interval

## Slide 6: QSE PRR525 10-Minute Interval Scoring

## Slide 7: March 2007 Resource Plan Performance Metrics

## Slide 8: 525 Passing 10-Min Interval Percentage Trends

## Slide 9: ERO / RE Activities
Entity Registration
  March 30th – Latest draft list submitted to NERC (work-in-progress)
  April 12th & 13th – NERC issued letters to all owners, operators, & users of the ERCOT Bulk Power System identified by ERCOT Compliance
  Any entity can challenge its listing and function with NERC
April 19th – FERC approved the Texas Regional Entity Delegation Agreement
May 11th – Submit 1st draft of 2008 Texas RE Business Plan & Budget to NERC
June 4th – NERC Reliability Standards take effect; mandatory compliance begins

## Slide 10: October 3, 2006 Event Status of Corrective Actions
LaaR Performance
  Seven Protocol Violation Notices issued
    Six notices related to Section 6.5.4(2) – tripping requirements for LaaR
    Summary of corrective actions
      Additional training provided to QSE Operators – training material and signed statements from Operators provided
      New procedures developed that automate notification process – Operator training and sign-off provided
      Performed drill sequences
      Training provided to LaaR with emphasis on the importance of deploying LaaR per Protocols
      Received certification statements from LaaR that related Protocols requirements had been read and understood
      Faulty breaker identified and replaced by one LaaR

## Slide 11: October 3, 2006 Event Status of Corrective Actions
LaaR Performance (Continued)
    One notice related to Section 6.5.1.1(4) – telemetry requirements
    Corrective action
      Replaced UPS requiring manual reset with UPS that automatically resets after power outages
  All corrective actions completed

## Slide 12: December 22, 2006 Event Status of Corrective Actions
Generator Trips
  Ride-through capability of generators during disturbances
    Violation Notice issued to Generator Owner for non-compliance with an ERCOT Operating Guides Requirement – Operating Guide 3.1.4.6
    Corrective actions
      Continuing to discuss corrective action plan with Generating Entity
      Generating Entity has hired a consultant to review plant relaying – preliminary results has indicated a relay setting problem
      Additional documentation and mitigation schedule received on April 13th

## Slide 13: December 22, 2006 Event Status of Corrective Actions
LaaR performance
  ERCOT Operations has requested that LaaR retest under-frequency relays that did not trip automatically
    7 QSEs – 61 LaaR
    Testing to be completed by May 9th
    Testing to be identical to initial qualification testing
  Three Protocol Violation Notices issued
  Summary of corrective actions
    One notice related to Section 6.5.4(2) – tripping requirements for LaaR
      Simultaneous telephone notification of all LaaR
      Manually triggered EMS audio alarm signal telemetered to all LaaR
      Manual tripping of one LaaR if it has not begun to ramp down 5 minutes after notification

## Slide 14: December 22, 2006 Event Status of Corrective Actions
LaaR Performance (Continued)
  Two notices related to Section 6.5.1.1(4) – telemetry requirements
  Summary of corrective actions
    Meeting between QSE and LaaR to re-emphasize requirements, review issues, and develop corrective actions
    Identified and replaced failed transducers
    Suspended participation by violating LaaR until corrective actions taken
    Full-time field manager position created to ensure performance of resources
  Required corrective actions largely completed – some additional validation required
    Non-performing LaaR to test to validate that corrective actions working
    New full-time field manager position not yet filled

## Slide 15: Wind-Only Portfolio Performance
10-minute average scores for wind-only portfolios have ranged from 5 to 60.
March 29th – Requests for Information issued to 5 wind-only QSEs and ERCOT ISO.
Attempt to understand what efforts and activities QSEs are undertaking to improve their wind-only portfolios’ performance.
April 11th – All responses received by ERCOT Compliance – responses forwarded to ROS Chair.
Compliance to participate as needed and monitor progress.

## Slide 16: CPS1 Performance
Performance monitoring criteria (PRR 525) implemented in January 2005 – steady CPS1 score improvement for first 6 months
  CPS1 performance peaked in June 2006 – 154.6
PRR 661 – Effective July 1, 2006 – SCE Performance Charge replaces disqualification
PRR 662 – Effective July 1, 2006 – 1) Allowed additional exemptions to QSEs, and 2) excluded uncontrollable renewable resources from complying with the metric
QSEs removed wind resources from portfolios and placed in new wind-only sub-QSEs

## Slide 17: CPS1 Performance
Declining performance expected during shoulder months (March/April & October/November)……….
  Fewer generating units on line because of lower demand
  Many generating units are cycled daily (turned on to meet load demand and later turned off when load subsides)
  3,000 MW (nameplate) of wind generation in ERCOT makes up a larger percentage of on-line generation
  March CPS1 score – 120.6; expect similar score in April
Performance should begin to improve again in May – if not………………….