## Slide 1: EDS 1 – ROS Update Early Delivery Systems
ROS Meeting
May 10, 2007

## Slide 2: EDS 1 – Early Delivery Systems
Agenda
  EDS 1 ROS Update
    Beta Testing Results
    Point-to-Point Estimates and Assumptions
    Point-to-Point Schedule

## Slide 3: EDS 1 – Early Delivery Systems
Beta Testing Results
  Testing Completed (Friday April 20th, 2007)
    14 of 16 TSPs participated
    19 of 22 QSEs participated
    90% complete - 2200 points checked out of 2400 planned
    10% errors found (non-quality code related)
  Error Summary
    Missing equipment on ERCOT Network Model = 20
    Missing, mis-mapped or indirectly mapped points = 198
    Polarity reversed = 7
    Quality Code (not counted in the 10% errors found)
      Field Telemetered = 253
      Non-field Telemetered = 277

## Slide 4: EDS 1 – Early Delivery Systems
Point-to-Point Estimates and Assumptions
  Estimating Metrics
    Existing Zonal points = 76,000 points
    3,500 stations
    16 TSPs
    22 QSEs (represents aggregated QSEs)
      500+ unit resources
      100+ load resources
  Estimating Assumptions
    Each point will take 1 minute to verify (on average)
    Unit and Load resources
      Each will add 30 additional Nodal points
      Total additional Nodal unit and load points = 20,000 points
    Total Nodal points to verify = 96,000 points

## Slide 5: EDS 1 – Early Delivery Systems
Point-to-Point Schedule
  Testing Begins Monday June 4, 2007
    June - CenterPoint Energy and TXU (TSP) verifications
    July - first stage of QSE verifications
    August - second stage of QSE verifications + TSP verifications
    September - remaining QSE and TSP verifications
  Preparation
    Review the ICCP Handbook
    Attend ERCOT WebEx meetings (contact Craig Dillon – cdillon@ercot.com)
    Work with the ERCOT ICCP group 2 weeks before verification:
      Create new associations with ERCOT
      Submit Service Request to build-up Nodal point database
  Scheduling
    EDS team is contacting each TSP and QSE to confirm schedule
    http://nodal.ercot.com - Readiness Center tab, Key Documents
      EDS 1 Weekly Status Report – contains detailed schedule