ERCOT OPERATIONS REPORT

ON THE

EECP EVENT

OF

March 09, 2007

Executive Summary	3

Time Line and Description of Significant Events	4

Observations/Data Review...........................................................................................5

Lessons Learned.........................................................................................................11

### Executive Summary

ERCOT implemented Step One of its Emergency Electric Curtailment Plan (EECP) on March 09, 2007.  Factors that led to ERCOT implementing the EECP Step One:

At 09:32:00 an Advisory was issued for Adjusted Responsive Reserve (ARR) below 3000 MW.

At 10:05:00, ERCOT declared an Alert for ARR below 2500 MW.

At 18:54:00 as ARR declined, ERCOT declared EECP step 1.  The Total ERCOT Telemetered SCE was -254 MW at this time - which was predominantly Wind QSEs.

The ERCOT evening load pickup climbed 1,682 MW in one hour, starting at 18:00 and leveling off at 19:14:00 at approximately 33,480 MW.

Day-Ahead Replacement Reserve Services (RPRS) planned on-line capability for hour ending 19:00 indicated the maximum capability of the system to be 37,903 MW.  However the indicated real-time capability at that hour was only 35,761 MW.  This shows to be a difference of 2,142 MW of expected capacity not present.

Wind output for hour ending 19:00 indicated the day-ahead resource plan of 681 MW and real-time output as 36 MW.

Two units were requested for quick start at 19:15 for a minimum run time of 2 hours, from 20:00 to 22:00.

As ARR recovered, EECP was terminated at 20:20.

Time Line and Description of Significant Events

- 09:32:00 Advisory Issued due to ARR below 3000 MW.

- 10:05:00 Alert issued due to ARR below 2500 MW.

- 18:54:00 Implemented EECP 1 due to ARR at 2,244 MW.

- 19:00:00 Several QSEs called to inform ERCOT of additional available resources and start times if needed.

- 19:15:00 VDI sent to two units (208 MW) to come online that were available for interval ending 20:00 until hour ending 22:00.

- 19:17:00 Spoke with SPP in regards to for Emergency assistance due to ERCOT being in EECP. SPP informed ERCOT to ask a QSE for schedule with Emergency Reservation.

- 19:17:00 Called a QSE to make request for Emergency Assistance of 200MW across the DC Tie.

- 19:33:00 The QSE called to inform that they would begin ramping at 19:37:00 with the 200 MW schedule.

- 19:35:00 SPP called to inform that before they could approve the schedule that ERCOT would have to post the request for Emergency assistance in the RCIS - informed shift supervisor and shift supervisor posted notice in the RCIS.

- 20:17:00 QSE was informed to end the schedule for Emergency Assistance.  The effective end time would be 20:30.

- 20:20:00 Terminated EECP 1. Alert still in effect. ARR at 2,880 MW. DC Tie will slowly start ramping out at 20:30. Quick start units VDI will end at 22:00 due to min run times.

Observations/Data Review

3/9/07 18:00 – 20:30 ARR, RRS, AND LOAD

18:00 – 20:30 1-HOUR-AVERAGE RPRS CAPACITY

AND 1-HOUR-AVERAGE REALTIME (CURRENT) CAPACITY

18:00 – 20:30 1-HOUR AVERAGE RESOURCE PLAN

AND 1-HOUR AVERAGE REAL-TIME OUTPUT OF WIND UNITS

18:00 – 20:30 ARR, RRS, AND TOTAL SCE

18:00 – 20:30 FREQUENCY AND REGULATION

18:00 – 20:30 FREQUENCY AND NONCONFORMING LOADS

Lessons Learned

Replacement Reserve Services (RPRS) uses the planned output of wind; these numbers are not usually reflected in the real-time schedules.

ERCOT Procedures for posting EECP notices on the RCIS needs to be updated.