## Slide 1: RTCAM Trial Period Update
ROS May -10, 2007

## Slide 2: Congestion on April 16th
Resource Outages affected the North – South flow
Temple-Pecan Creek 345 Dckt was the binding constraint
QSEs in North moved down while QSEs in South were moved up

## Slide 4
DTMPTHS5: Lake Creek – Temple Switch / Tradinghouse – Temple Pecan Creek 345 kV Dckt
Overload: Lake Creek – Temple Pecan Creek 138 kV
Direction of Flow is North to South

## Slide 5: Observations
RTCAM computed correct OC3s
SPD used OC3s to dispatch generation rather than OC2s.
The OC3 shift factors are computed from the real-time network model while OC2s are computed from historical off-line studies.
The same units are dispatched in both; The primary difference is more accurate shift factors with OC3s.
RTCAM compares the real-time status to the QSE Resource Plan status
  Resource plans needed to be updated in some cases to reflect actual unit status
Multiple QSEs requested Ancillary Service exemptions under 6.6.4 Obligations to Honor Ancillary Service Commitments
  In some cases the QSE requesting the exemption had all of their AS on one generator.
  In some cases a QSE was issued multiple unit specific deployments

## Slide 6: Summary
RTCAM has run in production for approximately 90 hours
ERCOT should consider creating a North – South CSC
Many generators impact Temple-Pecan Creek 345 Dckt
Constraint using OC3s delivered similar results as using OC2s
Control of congestion with manual OOME would possibly limit the number of units involved but would still impact AS delivery and would not be as economical.
Same problem can exist in Nodal, however under Section 5.5.2 paragraph (7) & Section 6.4.8.1.2 ERCOT can analyze deliverability of AS and inform the QSE that a resource does not qualify to deliver AS and it must be provided from a different resource or via a bilateral arrangement. No such language in Zonal exist.