## Slide 1: Replacement Reserve Non-Spin Flag Code Implementation
ROS 5/10/2007

## Slide 2: Non-Spin Units in Replacement Prior to Code Implementation
Units that QSEs planned to set aside to meet their Non-Spin Obligation were procured by Replacement in some cases
  In Some of these cases, during deployment of Non-Spin, QSEs have asked ERCOT to relieve them of their Non-Spin Obligation per protocol 6.6.4 .
Non-Spin Obligation was not part of the Capacity Requirements in the Replacement Reserve Studies
  Replacement Reserve would ensure that ERCOT could meet the Load Forecast Demand, Regulation Up & Responsive Reserve but did not include the Non-Spin capacity obligation
Non-Spin Obligation can be met by on-line or off-line units
  ERCOT could not determine the percent of Non-Spin capacity that QSEs were providing from off-line units

## Slide 3: After Code Implementation
Off-line Non-Spin units that could be started in 30 minutes or less and had their Non-Spin flag checked, were shown online in the Replacement Study.
The Non-Spin Capacity Obligation was added to the System Capacity Obligations
Replacement Reserve could utilize the Non-Spin units to solve congestion in the study.
  Change in Philosophy
Operators had to deploy the Non-Spin resources in real-time per protocol 6.7.4 paragraph 2, in order to solve local congestion in some areas.
  Deployments of Non-Spin to manage congestion occurred on May 8th & May 9th
  Currently a manual workaround process with no procedure in place to manage congestion in this manner

## Slide 4: Re-Run of May 7th Operating Day
The May 7th Operating day was re-run in study mode to determine how the procurements would have changed without the Non-Spin units shown online
  One Gas turbine was started for hours 19 – 23 & One Gas turbine was started for hours 19 – 23. Each unit was started for local congestion and had been shown online in the original Replacement Study.
  Six Gas turbines were started for hours 12 – 17 to satisfy power balance and these units had been shown online in the original Replacement Study.

## Slide 5: Summary
The code change was backed out for the May 10th Operating Day
Option 1 – Place code back in service and update the procedures to manually deploy (can not be automated) Non-Spin for local congestion
Option 2 – Keep the original design that doesn’t utilize the Non-Spin flag