Curtis Crews, ERCOT

RE: ERCOT Nodal ICCP Communication Handbook

General Comments

Section 3.3.3 dddd is an 8-character data descriptor   Should be a 4-character (same issue in 4.4.1.1)

Table 3 has 2 data descriptors with only 3 character (CUP and CDN) is there an underscore missing or?

Do we indicate what should be fillers?

Are there any TSP values that can be in this table?  Breaker status?

In 3.5.2  Is there an accepted value for “Current” (i.e. Amps)?  Some TSPs provide amps for lines (TXU dynamic ratings are provided this way).

3.5.3 Is there a Generator sign convention (don’t laugh…)?  SVCs, statcoms, synchronous condensers conventions?  Megawatts in DC Injection is spelled incorrectly.  Are there Raise/Lower sign conventions for transformer taps?

In 4.2 it says QSE must submit Attachment A, B, and C.  In 4.3 it says Attachment A, B, C, and D.  Which is right?

Also, the AIEF and associated forms should be referenced

The AEIF instructions indicates a “Network Information Form” but the Table 18 title indicates ‘Network-wide Information From” (same thing in TSP section 5.3 execpt table 35 reference)   why is the version of the AIEF fro QSEs 1.0 and for TSPs .01?

Tables 19, 20 and 21 does not show the real IP address does it?  I would hope this does NOT.  They are removed in Tables 36, 37, and 38.  Also, there is a difference in the MP address redacting.  I would recommend the XXXXX for all.

Is equipment type Bus (Table 17) or Buss (Table 22)

In Table 22 is Buss (or Bus) the Electrical Bus?  I agree that a typical Bus would be an Electrical Bus but……

In Table 23 would be nice to add “Text” to “Reason” when discussing limits (like in Table 32)?  By the way-  Who is saving these Text Reasons?

In Table 24, I assume by the description of Unit of Measure that Celsius is the scale?  Is that clearly stated anywhere?

In Table 27 is it ‘Base Point” or “Basepoint”?

Please explain the “Per-Bus” Tables 28 and 29.  I would think that this is not a 4 second frequency requirement since LMPs will not be calculated except during execution of SCED.

Table 29 should say “Load Zone” vs “Load zone”

In Table 32 there is a tap position requirement that is not defined in Table 23.

Table 23 needs to have Net and Gross MVAR and MW listed.

Breaker status is defined in Table 32 but not in Table 23. needs added.

There is a “Generation Resource DSR Schedule” listed in Table 32 but only a “Dynamically scheduled resource” listed in Table 23 with a measurement unit of status.  Table 23 probably needs to add the schedule while 32 needs to add the status.

I did not see it but we need Voltage readings where applicable for resources  (especially if the resources own transmission level equipment).

In 4.3 AIEF you have a contact name but in 5.3 there is not one.  Should there be or a general caveat like the Ted Hailu reference????

Table 35 should have the Domain Name for the TSP as “NTSP” not “QSE”

The ICCP Object Name Example for Bus Hz (Table 39) indicates voltage.  For Transformer Mvars indicates TAP.

In general I would say there are no MW or MVA readings for capacitors and reactors(Table 53).

Statcom and SVCs are not listed but should be.  “Amps” are provided by some companies such as TXU…are these NOT allowed in Nodal?

Table 40 Buss or Bus???

Table 41 and 42 does not have status but table 39 does.

Table 43 should also indicate Capacitor MVAR.

Table 44 should be every switch not just circuit breakers.

Table 46 has MVAR for DC but Table 39 does not.

Table 39 ignores BLTs (refer to Table 47).  Understand that BLTs may be classified as generation resources (I do not know).  This does not appear to be captured.

Table 39 ignores Weather Zones (Table 48)…should be included.

I do not think that is envisioned that a TSP will provide the data listed in 5.4.4 and Table 49 as ICCP exchanged data.  Please verify with Jay Dondeti.

Table 52 Ratings will not be calculated by the MW/MVAR pair.  These are calculated by the Dynamic Ratings processor using the tables provided.  Table 52 ratings are calculated locally using the data provided by TSPs.

Attachment A was not there???

______________________________________________________________________________

Dana Showalter, ERCOT

RE: ERCOT Nodal ICCP Communication Handbook

General Comments

We have changed WAN providers and no longer use Frame Relay as the communications protocol but instead use Mulit-Protocol Label Switching (MPLS). This affects your document quite a bit - graphics, wording, etc. I also found out that the Appendices are not current either. The current version uses a table format in Word, available from Wholesale Client Services. Please be aware, this document also needs to be freed of references to Frame Relay.