## Slide 1: McCamey Area Limits
Current Procedure
Impacts To Study
Q&A
Conclusion

## Slide 2: Current Procedure Flow
Power Flow Analysis
  Build base case
    Determine next day’s peak hour using load forecast
    Use peak hour load and generation plan
    Include scheduled outages for peak hour
      most Clear any base case violations where Normal Rating ≥ 100%.
  Save as STNET case: x_basecase_mmddyy_initials
Notes: Usually the study hour is changed from peak hour to 16:00 since inside outage window. Why? Because, we’re not studying every hour, and we are looking for the worse case scenario.
This saved base case is used to calculate the wind and CSC limits.
Next, to begin determining the wind limits, adjust…

## Slide 3
Adjust McCamey wind generation units’ output based on their capacity-ratio-share until a base case or post-contingency emergency rating violation ≥ 100% appears.
  If the rating is > 100% reduce the McCamey wind generation to achieve a 100% base case or post-contingency 2hr rating.
  When the base case or post-contingency violation(s) reach 100% this is the limit.
Current Procedure Flow
Notes: As we move to the next slide, keep in mind that current our A,B, and C ratings are generally the same! (100% ; A=B=C)

## Slide 4
Current Procedure Flow
Wind Unit Limitations (S7) – Limits are established to support voltage requirements in the area.
Wind Unit Name | Capacity | Limit
SW_MESA_SW_MESA | 75 | 67
WOODWRD1_WOODWRD1 | 83 | 75
INDNNWP_INDNNWP (RRWF) | 83 | 82
INDNENR_INDNENR (RRWF) | 84 | 83
INDNENR_INDNENR_2 (RRWF) | 77 | 76
KING_SW_KINGSW | 79 | 71
KING_NW_KINGNW | 79 | 71
WOODWRD2_WOODWRD2 | 77 | 69
KING_SE_KINGSE | 40 | 36
KING_NE_KINGNE | 79 | 71
Total | 756 | 701
Notes: Of course, currently with most norm/emergency/load shed line ratings being equal, Limit A and B will be the same.
For the ratings that
Now, limit A ~ limit B… what does that mean.
Let’s look at how wind generation is allocated using these 2 limits…

## Slide 5: Impacts to Study
Area Generation
Transmission Outages

## Slide 6: Question: Are the “TGR” limits that are developed in the Day Ahead envisioned by the protocols? (If not, why isn’t the language boxed?)
Answer:
Yes, per Protocols Section 7.8.1 and 7.8.2, ERCOT calculates “TGR” limits in the day ahead and posts this information on the ERCOT website.
Q&A

## Slide 7: Question: Are entities performing at or below the limits that have been developed in the Day Ahead process? For instance, slow movers are not allowed to operate above their targets per Protocol 7.8.9(4).
Answer:
The McCamey area wind farms do an excellent job at operating at or below their share of the TGRs.
If they do generate above their allocated limit, they are called and asked to back down to their limit.
Q&A

## Slide 8: Question: Are the fast movers (RRWF) responding quickly when asked to reduce their output?
Answer:
The ERCOT Operators have stated that the “Rapid Responders” are following their instructions in accordance with Protocol 7.8.9 (5).
Q&A

## Slide 9: Question: When the limit in RT is less than the limit calculated in the Day-Ahead, are required reductions to the rapid response wind farms allocated pro rata as stated in Protocols 7.8.9(7)?
Answer:
Yes, as stated in Protocols Section 7.8.9(7) ERCOT instructs the fast movers to reduce their output and after an hour the slow movers are issued a VDI to reduce their output and the fast movers are allowed to increase their output up to their TGR allocation.
Q&A

## Slide 10: Question: Protocols section 7.8.9(8) requires that wind farms are not entitled to OOME down payment in excess of TGRs. Is anyone evaluating this requirement in settlements?
Answer:
According to Settlements, ERCOT does not pay any OOME down in excess of the TGR or resource plan, whichever is minimum. For example, if the TGR is 25MW, Resource Plan is 30MW and the generator is at 50MW, any OOME down payments are from the TGR level to the instructed level.
Q&A

## Slide 11: Questions?
Notes: Our goal is continued efforts to streamline our process to further increase the accuracy of all calculated limits.