ERCOT Nodal Protocols

Section 10:  Metering

February 1, 2007

(Effective Upon Texas Nodal Market Implementation)

METERING	4

10.1	Overview	4

10.2	Scope of Metering Responsibilities	4

10.2.1	QSE Real-Time Metering	4

10.2.2	TSP and DSP Metered Entities	4

10.2.3	ERCOT-Polled Settlement Meters	5

10.2.3.1	Entity EPS Responsibilities	6

10.3	Meter Data Acquisition System (MDAS)	6

10.3.1	Purpose	6

10.3.2	ERCOT-Polled Settlement Meters	7

10.3.2.1	Generation Meter Splitting	7

10.3.2.1.1	Generator Metering Real-Time Splitting Signal	7

10.3.2.1.2	Allocating EPS Metered Data to Generator Virtual Meters	8

10.3.2.1.3	Processing for Missing Dynamic Splitting Signal	8

10.3.2.1.4	Calculating the Virtual Generator Ratio	8

10.3.2.1.5	Generation Splitting Data Made Available to Market Participants	9

10.3.2.1.6	Allocating EPS Metered Data to Generator Owners When It Is Net Load	9

10.3.2.2	Loss Compensation of EPS Meter Data	9

10.3.2.3	Generation Netting for EPS Meters	9

10.3.2.4	Reporting of Net Generation Capacity	10

10.3.3	TSP or DSP Metered Entities	11

10.3.3.1	Data Responsibilities	11

10.3.3.2	Retail Load Meter Splitting	11

10.3.3.2.1	Retail Customer Load Splitting Mechanism	12

10.3.3.2.2	TSP and DSP Responsibilities Associated with Retail Customer Load Splitting	12

10.3.3.2.3	ERCOT Requirements for Retail Load Splitting	13

10.3.3.3	Method for Interfacing with MDAS	13

10.3.3.3.1	Past Due Data Submission	13

10.4	Certification of EPS Metering Facilities	13

10.4.1	Overview	13

10.4.2	EPS Design Proposal Documentation Required from the TSP or DSP	13

10.4.2.1	Approval or Rejection of an EPS Design Proposal for EPS Metering Facilities	14

10.4.2.1.1	Unconditional Approval	14

10.4.2.1.2	Conditional Approval	14

10.4.2.1.3	Rejection	15

10.4.3	Site Certification Documentation Required from the TSP or DSP EPS Meter Inspector	15

10.4.3.1	Review by ERCOT	15

10.4.3.2	Provisional Approval	16

10.4.3.3	Obligation to Maintain Approval	16

10.4.3.4	Revocation of Approval	16

10.4.3.5	Changes to Approved EPS Metering Facilities	16

10.4.3.6	Confirmation of Certification	17

10.5	TSP and DSP EPS Meter Inspectors	17

10.5.1	List of TSP and DSP EPS Meter Inspectors	17

10.5.2	EPS Meter Inspector Approval Process	17

10.5.2.1	TSP and DSP Responsibilities	17

10.5.2.2	ERCOT Responsibilities	17

10.6	Auditing and Testing of Metering Facilities	18

10.6.1	EPS Meter Entities	18

10.6.1.1	ERCOT Requirement for Audits and Tests	18

10.6.1.2	TSP and DSP Testing Requirements for EPS Metering Facilities	18

10.6.1.3	Failure to Comply	19

10.6.1.4	Requests by Market Participants	19

10.6.2	TSP and DSP Metered Entities	19

10.6.2.1	Requirement for Audit and Testing	19

10.6.2.2	TSP and DSP Requirement to Certify per Governmental Authorities	19

10.7	ERCOT Request for Installation of EPS Metering Facilities	20

10.7.1	Additional EPS Metering Installations	20

10.7.2	Approval or Rejection of Waiver Request for Installation of EPS Metering Facilities	20

10.7.2.1	Approval	20

10.7.2.2	Rejection	20

10.8	Maintenance of Metering Facilities	21

10.8.1	EPS Meters	21

10.8.1.1	Duty to Maintain EPS Metering Facilities	21

10.8.1.2	EPS Metering Facilities Repairs	21

10.8.2	TSP or DSP Metered Entities	21

10.9	Standards for Metering Facilities	22

10.9.1	ERCOT-Polled Settlement Meters	22

10.9.2	TSP or DSP Metered Entities	23

10.9.3	Failure to Comply with Standards	23

10.10	Security of Meter Data	24

10.10.1	EPS Meters	24

10.10.1.1	TSP and DSP Data Security Responsibilities	24

10.10.1.2	ERCOT Data Security Responsibilities	24

10.10.1.3	Resource Entity Data Security Responsibilities	25

10.10.1.4	Third Party Access Withdrawn	25

10.10.1.5	Meter Site Security	25

10.10.2	TSP or DSP Metered Entities	25

10.11	Validating, Editing, and Estimating of Meter Data	25

10.11.1	EPS Meters	25

10.11.2	Obligation to Assist	26

10.11.3	TSP or DSP Settlement Meters	26

10.12	Communications	26

10.12.1	ERCOT Acquisition of Meter Data	26

10.12.2	TSP or DSP Meter Data Submittal to ERCOT	26

10.12.3	ERCOT Distribution of Settlement Meter Data	26

10.13	Meter Identification	27

10.14	Exemptions from Compliance to Metering Protocols	27

10.14.1	Authority to Grant Exemptions	27

10.14.2	Guidelines for Granting Temporary Exemptions	27

10.14.3	Procedure for Applying for Exemptions	28

10.14.3.1	Information to be Included in the Application	28

# 10	METERING

10.1	Overview

(1)	This Section specifies the responsibilities and requirements for meter data, certification of Metering Facilities, meter standards, approved meter types and the process for auditing, testing, and maintenance of Metering Facilities to be used in the ERCOT Region.  “Metering Facilities” means Revenue Quality Meters, instrument transformers, secondary circuitry, secondary devices, meter data servers, related communication Facilities and other related local equipment intended to supply ERCOT settlement quality data.

(2)	Transmission Service Providers (TSPs) and Distribution Service Providers (DSPs) are the only Entities authorized to provide Settlement Meter data to ERCOT.  ERCOT shall maintain a Meter Data Acquisition System (MDAS) to collect generation and consumption energy data for settlement purposes under these Protocols.  The MDAS must receive Customer Load meter data from TSPs and DSPs and must collect data from all ERCOT-Polled Settlement (EPS) Meters.

(3)	All Service Delivery Points (SDPs), excluding EPS, All-Inclusive Generation, or Non Opt-In Entity (NOIE) metering points, that meet the requirements of P.U.C.T. Subst. R. 25.311 are eligible for competitive meter ownership pursuant to such PUCT Substantive Rule.  All competitively owned meters shall meet all the applicable metering requirements of the ERCOT Protocols and Competitive Metering Guides.

10.2	Scope of Metering Responsibilities

10.2.1	QSE Real-Time Metering

The Qualified Scheduling Entity’s (QSE’s) responsibility for Real-Time metering requirements is contained in Section 6.5.5.2, Operational Data Requirements. .

10.2.2	TSP and DSP Metered Entities

(1)	Each TSP and DSP is responsible for supplying ERCOT with meter data associated with:

(a)	All Loads using the ERCOT System;

(b)	Any All-Inclusive Generation Resource that delivers less than 10 MW to the ERCOT System and that is connected directly to the distribution system; a DSP may make some or all such meters ERCOT-Polled Settlement (EPS) compliant and may request that ERCOT poll the meters. Notwithstanding the foregoing sentence, meter data is not required from:

(i)	Generation owned by a NOIE and used for NOIE’s self-use (not serving Customer Load); and

(ii)	Renewable generation with a design capacity less than 50 kW interconnected to a DSP and not registered as a Generation Resource; and.

(c)	NOIE points of delivery where metering points are radial Loads and are unidirectionally metered.  A TSP or DSP has the option of making some or all such meters EPS compliant and to request that ERCOT poll the meters.

(2)	Each TSP and DSP is responsible for the following:

(a)	Compliance with the procedures and standards in this Section, the Settlement Metering Operating Guides (SMOG) and the Operating Guides;

(b)	Installation, control, and maintenance of the Settlement Metering Facilities, as more fully described in this Section and SMOG, which includes meters, recorders, instrument transformers, wiring, and miscellaneous equipment required to measure electrical energy;

(c)	Costs incurred in the installation and maintenance of these Metering Facilities and communications except for incremental costs incurred for functions not required for the settlement of the Load or All-Inclusive Resource.  These incremental costs shall be borne by the Entities requesting the service pursuant to the TSP or DSP tariffs; and

(d)	Installation, maintenance, data collection, and related communications, telemetry for the Metering Facilities, and related services necessary to meet the mandatory Interval Data Recorder (IDR) requirements detailed in this Section, Section 18, Load Profiling, and the SMOG.

10.2.3	ERCOT-Polled Settlement Meters

(1)	ERCOT shall poll Metering Facilities that meet any one of the following criteria:

(a)	Generation connected directly to the ERCOT Transmission Grid;

(b)	Auxiliary meters used for generation netting by ERCOT;

(c)	Generation delivering 10 MW or more to the ERCOT System;

(d)	Generation participating in any Ancillary Service market;

(e)	NOIE points connected bi-directionally to the ERCOT system; and

(f)	Direct Current Ties.

(2)	Additionally, ERCOT shall poll any All-Inclusive Generator or NOIE metering point at the request of such Entity, provided the Metering Facility meets all requirements and approvals associated with EPS metering requirements of this Section and the SMOG.  Load Resources of 10 MW or more on the ERCOT System, may, at their option have an EPS meter.

10.2.3.1	Entity EPS Responsibilities

The following defines the responsibilities of Entities regarding EPS metering:

(a)	EPS Meters must be polled directly by ERCOT, which shall then convert the raw data to Settlement Quality Meter Data in accordance with this Section, Section 11, Data Acquisition and Aggregation, and the SMOG.

(b)	A TSP or DSP shall have EPS Metering Facilities installed and maintained under the supervision of a TSP or DSP “EPS Meter Inspector,” which is defined as an employee or agent of the TSP or DSP who has received EPS training from ERCOT, and is described further herein.

(c)	Each TSP and DSP shall install, control, and maintain the meters, recorders, instrument transformers, wiring, communications, and other miscellaneous equipment required to measure electrical energy, as described in this Section and SMOG.

(d)	Each TSP and DSP shall install and maintain a Back-up Meter(s)at each EPS Meter location for Resources, auxiliary netting, and bi-directional meter points.  A “Back-up Meter” is defined as a redundant revenue quality EPS Meter connected at the same metering point as the primary EPS Meter and meeting the requirements defined in the SMOG.

(e)	Costs incurred in the installation and maintenance of EPS metered Facilities and communications will be the responsibility of the TSP or DSP except for incremental costs incurred for functions not required for the energy settlement as required by these Protocols.  These incremental costs shall be borne by the Entities requesting the service, as per the TSP’s or DSP’s tariffs.

(f)	Specific operating practices for EPS Metering Facilities are included in the SMOG.

10.3	Meter Data Acquisition System (MDAS)

10.3.1	Purpose

The MDAS will be used:

(a)	By ERCOT to obtain and receive Revenue Quality Meter data from the EPS Meters and Settlement Quality Meter Data from the TSP and DSP for settlement and billing purposes; and,

(b)		To populate the ERCOT Data Archive used by Market Participants or their agents with authority to access Settlement Quality Meter Data held by ERCOT.

10.3.2	ERCOT-Polled Settlement Meters

(1)	Each TSP and DSP shall, in accordance with these Protocols and the SMOG, provide ERCOT-approved metering communication equipment and connection to permit ERCOT access to the TSP’s or DSP’s EPS Meters.

(2)	ERCOT shall retrieve meter data electronically and automatically by MDAS.  ERCOT may also collect meter data on demand.

10.3.2.1	Generation Meter Splitting

(1)	Each Generation Resource meter must be represented by only one QSE, except that a jointly owned Generation Resource unit or group of Generation Resources may split the net generation output into two or more virtual generating units for a Generation Entity.  Each Generation Entity representing a virtual generating unit may have its energy and capacity scheduled through separate QSEs.  For purposes of this paragraph, a jointly owned Generation Resource unit or group of Generation Resources shall also include the San Miguel and Gibbons Creek power projects, and intermittent Resources such as wind and solar generation.

(2)	When the Generation Resource unit is registered with ERCOT, the Entities representing virtual generator units shall be required to submit a percentage allocation of the Resource to be used to determine the capacity available at each virtual generator unit.

(3)	When the generator unit is registered with ERCOT, the owners of the unit shall submit all required ERCOT facility registration documentation and an ERCOT-approved splitting agreement executed by an authorized representative from each owning Entity.  Such agreement shall contain a defined and fixed ownership percentage as among the owning Entities.  ERCOT shall establish this generator as a “split,” essentially establishing a virtual generator meter.  Generation splitting based on a static ratio is not permitted.  Generation splitting requires Real-Time splitting signals.

##### 10.3.2.1.1	Generator Metering Real-Time Splitting Signal

(1)	When the split-metered generating unit is registered at ERCOT, the Entities representing the virtual generator units shall select one master QSE to provide ERCOT with a Real-Time signal of the MW of generation per virtual generator unit.  The signal must be sent from the master QSE’s EMS system to ERCOT via the appropriate telemetry.  The signal must be revised every scan cycle and must represent each virtual generator unit in positive MW.  The signal must contain the Resource ID (RID) and the MW assigned to that RID.

(2)	ERCOT shall integrate the signals and provide a MWh value for each 15-minute interval for each virtual generator unit.  The settlement system must use the MWh per interval value to calculate the percentage breakdowns to be applied to the actual metered MWh values retrieved from the EPS metered Entity.

##### 10.3.2.1.2	Allocating EPS Metered Data to Generator Virtual Meters

(1)	ERCOT shall poll the EPS Metering Facilities related to the actual Generation Resource and store the meter data at 15-minute intervals.  This metering data must be validated, edited, estimated, and compensated for losses, as necessary, and be netted as required.  This resulting data must then have the virtual generator ratios applied to assign the generation to the QSE representing each owner of the virtual generators.  The MWh quantities of the virtual generators must be used in all settlement calculations and reports.

(2)	The following example illustrates the splitting of the generation data:

Splitting Example 1

| Integrated values from ERCOT systems |  |  |  |  |  |  | Actual Metered MWh | Data to be Used in Settlement |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Interval Ending | RID1 (MWh) | RID2 (MWh) | RID3 (MWh) | Total MWh |  | % Ratios Rid 1,2,3 |  | Split MWh | Split MWh | Split MWh |
| 13:15 | 10 | 20 | 10 | 40 |  | 25, 50, 25 | 52 | 13 | 26 | 13 |

##### 10.3.2.1.3	Processing for Missing Dynamic Splitting Signal

For any interval when ERCOT has not received a Real-Time signal for any one of the virtual generating units, ERCOT shall use the last valid percentage ratio for a completed interval.

Splitting Example 2

| Integrated values from ERCOT systems |  |  |  |  |  |  | Actual Metered MWh | Data to be Used in Settlement |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Interval Ending | RID1 (MWh) | RID2 (MWh) | RID3 (MWh) | Total MWh |  | % Ratios Rid 1,2,3 |  | Split MWh | Split MWh | Split MWh |
| 13:15 | 10 | 20 | 10 | 40 |  | 25, 50, 25 | 52 | 13 | 26 | 13 |
| 13:30 | NA | 21 | 10 | NA |  | Ratio Above | 55 | 13.75 | 27.5 | 13.75 |
| 13:45 | NA | 22 | 10 | NA |  | Ratio Above | 48 | 12 | 24 | 12 |

##### 10.3.2.1.4	Calculating the Virtual Generator Ratio

(1)	For split-metered generating units, ERCOT shall provide for settlement the net MWh value for each 15-minute interval.  This value is the MWh accumulated based on the MW value over each scan cycle.  ERCOT shall use a standard “integration” mechanism to perform this function.

(2)	For settlement, ERCOT shall use the integrated data to determine the allocation ratio as the integrated share of each signal divided by the integrated total of signals.

##### 10.3.2.1.5	Generation Splitting Data Made Available to Market Participants

Market Participants shall have access to allocated generation output and ratio data only for virtual generators that they represent.  ERCOT shall provide the allocation ratio for that RID.  The master QSE for a split-metered generator unit shall have access to the allocation ratios and assigned generation output for units in which they act as the master QSE.

##### 10.3.2.1.6	Allocating EPS Metered Data to Generator Owners When It Is Net Load

EPS Generation Resource sites that are netted by ERCOT may have multiple Competitive Retailers (CRs) associated with the Load.  ERCOT shall poll the EPS metering facilities related to the actual Generation Resource facility and store the meter data at 15-minute intervals.  ERCOT shall perform validation, editing, estimation, compensation for losses as necessary, and netting as required for EPS metering data.  For intervals when data is net Load, the fixed ownership percentages stored in the asset database must be used to allocate the consumption to multiple Electric Service Identifier (ESI) IDs.  The consumption quantities for the ESI IDs must be used in all energy settlement calculations and reports.

10.3.2.2	Loss Compensation of EPS Meter Data

(1)	Where the EPS Meter is not located at the point of interconnection to the ERCOT Transmission Grid, actual metered consumption must be adjusted for line and transformation losses to the point of interconnection.  The preferred method for loss compensation and correction is via internal meter programming.

(2)	Recognizing the fact that some locations may not have the total functionality necessary to perform internal compensation, the Data Aggregation System (DAS) must have the functionality to perform approved loss compensation as necessary.  ERCOT shall retain the discretion to allow or deny the continued use of this type of metering.

(3)	No meter may be compensated internally for losses more than once.  ERCOT may compensate multiple meters prior to netting to the point of interconnection.  Pulse communications transfer of data between meters is not allowed.

10.3.2.3	Generation Netting for EPS Meters

(1)	At Generation Resource Facilities, generation and associated Load must be metered at their points of interconnection to the ERCOT Transmission Grid.  IDR meters must be used to determine generator output or Load usage.  In the intervals where the generation output exceeds the Load, the net must be settled as generation.  In the intervals where the Load exceeds the generation output, the net must be settled as Load and carry any applicable Load shared charges.

(2)	For settlement purposes, generation netting is not allowed except under one of the following conditions:

(a)	Single point of interconnection with delivered and received metering data channels;

(b)	Multiple points of interconnection where the Loads and generator output are electrically connected to a common switchyard, as defined below.  In addition, there must be sufficient generator capacity to serve all plant Loads for netting to occur;

(c)	A Qualifying Facility (QF) with point(s) of interconnection where the QF is selling to the QF’s thermal host(s) may net the Load meters of the thermal host with its generation meters when the Load and generation are electrically connected to a common switchyard.  In instances in which Load is served by new on-site generation through a common switchyard, the TSP or DSP may install monitoring equipment necessary for measuring Load to determine stranded cost charges, if any are applicable, as determined under Public Utility Regulatory Act (PURA) and applicable PUCT rules.  If the PUCT requires other Load served by onsite generators to pay the System Benefit Fund charges, then, in instances in which Load is served by generation through a common switchyard, the TSP or DSP may install metering equipment solely for purposes of the TSP’s or DSP’s calculation of System Benefit Fund charges, as provided by PURA, if any is applicable.  For purposes of this Section, new on-site generation has the meaning as contained in Public Utility Regulatory Act, Tex. Util. Code Ann. § 39.252 and     § 39.262(k) (Vernon 1998 & Supp. 2005) (PURA); or

(d)	For Generation Resources and/or Load with flow-through on a private, contiguous transmission system (not included in a TSP or DSP rate base) and in a configuration existing as of October 1, 2000, the meters at the interconnections with the ERCOT Transmission Grid may be netted for the purpose of determining Generation Resources or Load.  For Settlement purposes, when the net is a Load, the metered interconnection points must be assigned to the same Load zone and UFE zone.

(3)	For purposes of this Section, a common switchyard is defined as an electric substation facility where the point of interconnection for Load and Generation Resources are located at the same facility but where the interconnection points are physically not greater than 400 yards apart.  The physical connections of the Load to its point of interconnection and the Generation Resource to its point of interconnection cannot be Facilities that have been placed in a TSP’s or DSP’s rate base.

10.3.2.4	Reporting of Net Generation Capacity

All Generation Resource facilities with associated Load shall report to ERCOT before February 1st of each year their projected Net Generation capacity available to the grid for use by others during the June to August time period for the current calendar year and five subsequent years in the same format as the generation capacity reports provided to the PUC.

10.3.3	TSP or DSP Metered Entities

10.3.3.1	Data Responsibilities

Each TSP and DSP shall be responsible for the following:

(a)	Providing consumption data for each ESI ID and RID on a monthly basis according to the data timeliness and accuracy standards defined in this Section and in the SMOG;

(b)	Providing start date, stop date, ESI ID or RID, and consumption data in kWh as well as an identifier for “estimated” reads as applicable;

(c)	Submitting a single Demand value for each non-IDR ESI ID that has a demand register to ERCOT if, and only if, a Demand value is required for TSP or DSP tariffs or for CR Customer billing.  If the CR and TSP or DSP do not require a Demand value, then the TSP or DSP shall not submit a Demand value to ERCOT even if the meter has a demand register;

(d)	Validating, Editing, and Estimating (VEE) meter data according to the standards in this Section before submitting data to the settlement process;

(e)	Calculating consumption for any unmetered services by ESI ID and submitting such data monthly to ERCOT, subject to ERCOT audit.  These calculations must be made pursuant to TSP and DSP-approved tariffs; and,

(f)	Metering all Loads, unless the Load meets the following criteria:

(i)	Energy consumption by substation Facilities and equipment for the purpose of transporting electricity (e.g., substation transformers, fans, etc.).

(ii)	Unmetered energy consumption represented by an ERCOT-approved Load Profile.

10.3.3.2	Retail Load Meter Splitting

Retail Service Delivery Points with Loads above 1 MW may split their actual meter data into a maximum of four consumption values with each value being assigned a unique ESI ID; provided, however, that if a Customer is using Provider of Last Resort (POLR) or the “Price-to-Beat” retail service, such Customer may not split its meter signal among multiple CRs through this Section.

##### 10.3.3.2.1	Retail Customer Load Splitting Mechanism

Customer meter data may be split into separate ESI IDs by the installation of a programmable signal splitter that would take the master meter signal and split it into no more than four separate values that must at all times equal the total output of the master meter signal.  Splitting of Customer meter data must meet the following requirements:

(a)	The signal splitter may be programmed to split the Load in any way the Customer chooses, provided that such splitting results in positive Load;

(b)	The Customer, or its CR(s), shall provide the signal splitter and shall be responsible for all costs of installing, maintaining, and operating the signal splitter, any associated equipment, and communications;

(c)	The TSP or DSP shall be responsible for approving the specifications and installation of any signal splitting devices;

(d)	Interval Data Recorders shall be required on the master Customer Load meter and each of the split channels for verification and settlement purposes;

(e)	The TSP or DSP metering system recording such split signals (four  ESI IDs) may be required to be redundant if so provided by TSP or DSP tariffs;

(f)	The split signals must be recorded in Real-Time and cannot be altered or substituted later in time;

(g)	One Entity shall be designated to pay the total TSP and/or DSP charges for the Customer; and,

(h)	Switching of CRs for the individual split-metered Customers shall comply with the registration procedures in Section 19, Texas Standard Electronic Transaction (Texas SET).

##### 10.3.3.2.2	TSP and DSP Responsibilities Associated with Retail Customer Load Splitting

(1)	Each consumption value from a Customer Load split meter shall be assigned a separate ESI ID by the TSP or DSP.  Each ESI ID may be assigned to a separate CR.  The master meter may not be assigned an ESI ID.

(2)	The TSP or DSP shall send interval data for each ESI ID for the ERCOT settlement system.

(3)	The TSP or DSP shall be responsible for verifying that the sum of the split ESI ID IDR data equals the total IDR value from the master meter.

##### 10.3.3.2.3	ERCOT Requirements for Retail Load Splitting

(1)	ERCOT shall settle all ESI IDs in the same manner.

(2)	ERCOT shall not receive or process the IDR data associated with the master meter.

10.3.3.3	Method for Interfacing with MDAS

(1)	Settlement Meter data shall be submitted to ERCOT on a periodic cycle, but no later than monthly, using the Texas SET meter data exchange format.  Each TSP or DSP shall ensure that consumption meter data submitted to ERCOT is in intervals of:

(a)	15-minutes for those ESI IDs and RIDs served by IDRs and,

(b)	 Monthly or on an ERCOT-approved meter reading cycle for non-IDR meters.

(2)	The Settlement Quality Meter Data submitted by TSP or DSP must be in kWh and kVarh values (as applicable).

##### 10.3.3.3.1	Past Due Data Submission

ERCOT shall provide a report to the appropriate TSP and DSP for any ESI ID or RID for which consumption data has not been received in the past 38 days.  Upon receipt of the missing consumption data report, the TSP or DSP shall have two Business Days to submit the missing consumption data.

10.4	Certification of EPS Metering Facilities

Each TSP and DSP shall certify EPS Metering Facilities in a manner approved by ERCOT.

10.4.1	Overview

This Section describes the steps that a TSP or DSP shall use to certify each EPS Metering Facility and the steps ERCOT shall use to approve each EPS Metering Facility.  This Section also describes the manner in which EPS Metering Facility approval requests must be made to ERCOT.

10.4.2	EPS Design Proposal Documentation Required from the TSP or DSP

Before installation of new EPS Meters, TSP or DSP shall provide ERCOT with an EPS Design Proposal of the Metering Facilities being considered for ERCOT approval as EPS Meter Facilities. An “EPS Design Proposal” is the documentation required on the form available on the MIS Public Area. Included one line drawings must be dated, detailed, bear the current drawing revision number, and show all devices which contribute to the burden in the metering circuits..  Other information may also be required by ERCOT for review regarding the meter and related installation and Facilities; such additional information shall be promptly provided to ERCOT by the TSP or DSP upon request of ERCOT.

10.4.2.1	Approval or Rejection of an EPS Design Proposal for EPS Metering Facilities

ERCOT may unconditionally approve, conditionally approve, or reject an EPS Design Proposal.

10.4.2.1.1	Unconditional Approval

If ERCOT unconditionally approves an EPS Design Proposal, then ERCOT shall promptly notify the TSP or DSP that the EPS Design Proposal has been approved.  The TSP or DSP may then commence installation of the EPS Metering Facilities in accordance with the EPS Design Proposal.

10.4.2.1.2	Conditional Approval

(1)	Notification of Conditional Approval:

If ERCOT conditionally approves an EPS Design Proposal, then ERCOT shall promptly notify the TSP or DSP that the EPS Design Proposal has been conditionally approved.  It shall set forth in such Notice the conditions on which approval is granted and the time period in which each such condition must be satisfied by the TSP or DSP.

(2)	Ability to Satisfy Conditions:

If the TSP or DSP disputes any condition imposed by ERCOT, the TSP or DSP must promptly notify ERCOT of its concerns and provide ERCOT with the reasons for its concerns.  If the TSP or DSP provides ERCOT such Notice, ERCOT may amend or withdraw any of the conditions on which it granted its approval or ERCOT may require the TSP or DSP to satisfy other conditions.  ERCOT and the TSP or DSP shall use good faith efforts to reach agreement on accomplishing the installation.

(3)	Notification of Satisfaction of Conditions:

The TSP or DSP shall promptly notify ERCOT when each condition in the approval has been satisfied and provide to ERCOT any information reasonably requested by ERCOT as evidence that such condition has been satisfied.

(4)	Confirmation of Satisfaction of Conditions:

If ERCOT determines that a condition has been satisfied, then ERCOT shall provide the TSP or DSP written confirmation that the condition has been satisfied.

(5)	Unsatisfied Conditions:

If ERCOT determines that a condition has not been satisfied, ERCOT shall notify the TSP or DSP that it does not consider the condition satisfied and shall set out in such Notice the reason(s) that it does not consider the condition satisfied.  If, after using good faith efforts, ERCOT and the TSP or DSP are unable to agree on whether the condition is satisfied, either Entity may refer the dispute to the Alternative Dispute Resolution (ADR) Procedures as described in Section 20, Alternative Dispute Resolution Procedure.

10.4.2.1.3	Rejection

If ERCOT rejects an EPS Design Proposal, then ERCOT shall promptly notify the TSP or DSP that the EPS Design Proposal has been rejected and shall set forth the reasons for its rejection.  The TSP or DSP shall submit to ERCOT a revised EPS Design Proposal after receiving such Notice.  If ERCOT rejects for a second time an EPS Design Proposal submitted by a TSP or DSP with respect to the same or similar Notice issued by ERCOT as described above, then ERCOT and the TSP or DSP shall use good faith efforts to reach agreement on the requirements and disputed items.  In the absence of agreement either Entity may refer the dispute to the ADR Procedures as described in Section 20, Alternative Dispute Resolution Procedures.

10.4.3	Site Certification Documentation Required from the TSP or DSP EPS Meter Inspector

(1)	A TSP or DSP EPS Meter Inspector shall complete an ERCOT site certification form for each set of EPS Metering Facilities that it inspects.  The site certification form is the official form used to document whether EPS Metering Facilities meet ERCOT criteria.

(2)	The TSP or DSP EPS Meter Inspector shall promptly notify ERCOT and document any discrepancy between ERCOT approved EPS Design Proposal on file and the actual Metering Facilities inspected by the TSP or DSP EPS Meter Inspector.

(3)	The TSP or DSP shall provide the documents as outlined in SMOG for each set of EPS Metering Facilities being considered for ERCOT approval.

10.4.3.1	Review by ERCOT

(1)	ERCOT shall review the ERCOT site certification documentation prepared by the TSP or DSP EPS Meter Inspector within 45 days of receipt.  If ERCOT finds that this data is incomplete or demonstrates that the EPS Metering Facilities fail to meet the standards contained within this Section or the SMOG, ERCOT shall promptly provide written or electronic notice of the deficiencies to the TSP or DSP.

(2)	ERCOT shall notify the TSP or DSP of the approval of the Metering Facility.  ERCOT shall return the original schematic drawings, and the original ERCOT site certification form stamped by ERCOT as approved.  ERCOT shall retain a copy of these documents.

10.4.3.2	Provisional Approval

If ERCOT finds that the documentation: provided by the TSP or DSP is incomplete or demonstrates that the EPS Metering Facility fails to meet the standards contained within this Section and SMOG; then ERCOT may, elect to issue a provisional approval for the Metering Facility.  The terms and conditions on which such provisional approval is issued shall be at ERCOT’s discretion and shall be defined for the TSP or DSP.  ERCOT shall not issue an approval until such time as all of the conditions of the provisional approval have been fulfilled to the satisfaction of ERCOT.  ERCOT shall post any provisional approvals on the MIS Public Area on a quarterly basis.

10.4.3.3	Obligation to Maintain Approval

Once an EPS Metering Facility has been installed, it is the responsibility of the TSP or DSP to ensure that the EPS Metering Facility complies with the approval criteria referred to in this Section and the SMOG.

10.4.3.4	Revocation of Approval

(1)	ERCOT may revoke in full or in part any approval of Metering Facilities, including a provisional approval if:

(a)	ERCOT or a TSP or DSP EPS Meter Inspector demonstrates that all or part of the EPS Metering Facilities covered by that approval no longer meet the approval criteria for EPS Metering Facilities contained in this Section and the SMOG; and

(b)	ERCOT has given written Notice to the TSP or DSP stating that the identified EPS Metering Facilities do not meet the approval criteria and the reasons and that the TSP or DSP fails to correct the deficiency and satisfy ERCOT, within 30 days, that the EPS Metering Facilities meet the approval criteria.

(2)	If ERCOT revokes in full or part an approval of EPS Metering Facilities, the TSP or DSP may seek re-approval of the EPS Metering Facilities by requesting approval in accordance with this Section.

10.4.3.5	Changes to Approved EPS Metering Facilities

Each TSP and DSP shall notify ERCOT of any planned modifications or changes to be made to any EPS Metering Facilities that would affect the EPS Metering Facility’s approval, not less than ten Business Days prior to the intended implementation of the change.  Before the intended date of the change, ERCOT may request additional information from the TSP or DSP to demonstrate that the EPS Metering Facilities will still meet the applicable approval standards; the TSP or DSP shall promptly comply with such request for information.  ERCOT may at its discretion audit Metering Facilities to determine compliance.  The TSP or DSP shall provide ERCOT with meter specific program details, as downloaded from the meter, when the EPS Meter is programmed.

10.4.3.6	Confirmation of Certification

On the written request of ERCOT, the TSP or DSP shall provide ERCOT written or electronic confirmation that the Metering Facilities of each metered Entity that the TSP or DSP represents have been certified in accordance with this Section and the SMOG within five Business Days of receiving such a request from ERCOT.

10.5	TSP and DSP EPS Meter Inspectors

10.5.1	List of TSP and DSP EPS Meter Inspectors

ERCOT shall maintain a list of TSP and DSP EPS Meter Inspectors, and details related to ERCOT training to become a TSP or DSP EPS Meter Inspector.

10.5.2	EPS Meter Inspector Approval Process

10.5.2.1	TSP and DSP Responsibilities

(1)	Each TSP and DSP shall ensure that personnel performing EPS Meter Facility certification duties are approved EPS Meter Inspectors and comply with this Section and the SMOG.  A TSP or DSP EPS Meter Inspector is required to complete an ERCOT EPS Meter Inspector training session.

(2)	The TSP and DSP shall submit to ERCOT the following information for individuals performing EPS Metering Facility certification.

(a)	Name of individual;

(b)	Time period the individual has been testing Generation Resource or transmission interconnect metering points;

(c)	TSP or DSP statement indicating that the individual has the technical expertise to perform EPS Metering Facility certification; and,

(d)	Additional documentation as required by ERCOT.

10.5.2.2	ERCOT Responsibilities

(1)	ERCOT shall hold EPS Meter Inspector training sessions on a regularly scheduled basis.  Sessions must include information on the following:

(a)	Market responsibilities of EPS Meter Inspectors;

(b)	Documentation requirements for the site certification;

(c)	Overview of EPS Metering Facilities related topics and documents;

(d)	Protocols requirements;

(e)	SMOG requirements; and,

(f)	Technical requirements.

(2)	ERCOT shall issue a certificate of attendance to individuals upon completion of the EPS Meter Inspector training sessions.

(3)	ERCOT shall have the authority to revoke an individual’s involvement with EPS Metering Facility certification.

10.6	Auditing and Testing of Metering Facilities

10.6.1	EPS Meter Entities

10.6.1.1	ERCOT Requirement for Audits and Tests

ERCOT shall have the right to audit any EPS Metering Facility that it considers necessary or to request and witness a test carried out by a TSP or DSP EPS Meter Inspector.

10.6.1.2	TSP and DSP Testing Requirements for EPS Metering Facilities

(1)	At a minimum, the TSP and DSP EPS Meter Inspector shall conduct testing of EPS Meters on an annual basis, within the same month of each year as the previous year’s test.  Metering Facilities used in the ERCOT system for settlement must be tested pursuant to the TSP or DSP tariffs, the SMOG and these Protocols.

(2)	Instrument transformers used in settlement metering circuits must be tested using the following guidelines:

(a)	Magnetic Instrument Transformers do not require periodic testing as they have shown themselves to be stable per ANSI C12.1.;

(b)	Coupling Capacitor Voltage Transformers (CCVTs) shall, at a minimum, be tested for accuracy on a five year cycle, by the end of the fifth year after the previous test; and,

(c)	Fiber-optic Current Transformers (CTs) shall, at a minimum, be ratio tested on a five year cycle, by the end of the fifth year after the previous test. .

(3)	ERCOT may determine that periodic testing of CCVTs and fiber-optic CTs is not required once these devices have been proven to be stable.  If the devices have shown themselves to be unstable, ERCOT may discontinue the use of these devices for settlement purposes.

10.6.1.3	Failure to Comply

If an EPS Metering Facility fails to comply with ERCOT’s audit or test procedures, ERCOT shall issue a warning to the TSP or DSP responsible for such Metering Facilities.  If the TSP or DSP fails to comply with ERCOT’s recommendations in a reasonable time, as determined by ERCOT, ERCOT shall notify the PUCT or the appropriate Governmental Authority.

10.6.1.4	Requests by Market Participants

Market Participants shall follow appropriate Governmental Authority rules for requesting the testing of Metering Facilities.

10.6.2	TSP and DSP Metered Entities

10.6.2.1	Requirement for Audit and Testing

(a)	Audit and Testing by a TSP or DSP

Each TSP or DSP shall conduct (or engage a qualified Entity to conduct) audits and tests of the Metering Facilities of the TSP or DSP Metered Entities that it represents to ensure compliance with all applicable requirements of any relevant Governmental Authority.  Each TSP and DSP shall undertake any other actions that are reasonably necessary to ensure the accuracy and integrity of the meter data.

(b)	Audit and Testing Requests by an affected Market Participant

Subject to any applicable Governmental Authority requirements, an affected Market Participant shall have the right to witness an audit or test carried out by the TSP or DSP or its authorized representative.

10.6.2.2	TSP and DSP Requirement to Certify per Governmental Authorities

If a Governmental Authority has authority to certify meter installations, then the TSP or DSP shall comply with such regulations.

10.7	ERCOT Request for Installation of EPS Metering Facilities

10.7.1	Additional EPS Metering Installations

(1)	If ERCOT determines that there is a potential need to install additional EPS Metering Facilities on the ERCOT System, ERCOT shall notify the relevant TSP or DSP in writing or electronically.  ERCOT’s Notice must include the following information:

(a)	The location of the meter point at which the additional EPS Metering Facilities are required;

(b)	The projected installation date by which the relevant EPS Metering Facilities should be installed;

(c)	The reason for the need to install the additional EPS Metering Facilities; and

(d)	Any other information that ERCOT considers relevant.

(2)	A TSP or DSP that is notified by ERCOT of the potential need to install additional EPS Metering Facilities must:

(a)	Give ERCOT written confirmation of receipt of  Notice within three Business Days of receiving such Notice;

(b)	Submit an EPS Design Proposal to ERCOT within 45 Business Days of receiving such Notice.

(3)	The TSP or DSP may request a waiver to install additional Metering Facilities.

10.7.2	Approval or Rejection of Waiver Request for Installation of EPS Metering Facilities

ERCOT may approve, or reject a waiver request at ERCOT’s sole discretion.

10.7.2.1	Approval

If ERCOT approves a waiver request, then ERCOT shall promptly notify the TSP or DSP.

10.7.2.2	Rejection

If ERCOT rejects a waiver request, then ERCOT shall promptly notify the TSP or DSP and shall set forth the reasons for its rejection.  The TSP or DSP may submit to ERCOT a revised waiver request within 14 Business Days of receiving such Notice.  If ERCOT rejects for a second time a waiver request submitted by a TSP or DSP with respect to the same or similar Notice issued by ERCOT as described above, then ERCOT and the TSP or DSP shall use good faith efforts to reach agreement on the requirements and disputed items.  In the absence of agreement either Entity may refer the dispute to the ADR Procedures as described in Section 20, Alternative Dispute Resolution Procedures.

10.8	Maintenance of Metering Facilities

10.8.1	EPS Meters

10.8.1.1	Duty to Maintain EPS Metering Facilities

Each TSP and DSP shall maintain its EPS Metering Facilities to meet the standards prescribed by this Section and the SMOG.  If the EPS Metering Facilities of a TSP or DSP require maintenance to ensure that they operate in accordance with the requirements of this Section, SMOG, or any Governmental Authority, then the TSP or DSP shall notify ERCOT of the need for such maintenance.  The TSP or DSP shall also inform ERCOT five Business Days in advance of the time period during which such maintenance is expected to occur.  During that period, the TSP or DSP, or its authorized representative, after notifying ERCOT, shall be entitled to access sealed EPS Metering Facilities to which access is required in order to undertake the required maintenance.

10.8.1.2	EPS Metering Facilities Repairs

If an EPS Metering Facility requires repairs to ensure that it operates in accordance with the requirements of this Section, then the TSP or DSP shall immediately notify ERCOT of the need for repairing such Metering Facility.  If, however, operating conditions are such that it is not possible for the TDSP to notify ERCOT of the need for repairs, then the TDSP may make the necessary repairs and then notify ERCOT of the repairs prior to the end of the next Business Day.

(a)	Where no Back-up Meter exists or Back-up Meter data is unavailable, the TSP or DSP shall ensure that the metering point is repaired and operational within 12 hours of problem detection;

(b)	Where a functional and operational Back-up Meter exists, the TSP or DSP shall ensure that the metering point is repaired and operational within five Business Days of problem detection.

10.8.2	TSP or DSP Metered Entities

Each TSP and DSP shall maintain its Metering Facilities in accordance with the requirements of the relevant Governmental Authorities and according to this Section.

10.9	Standards for Metering Facilities

For settlement purposes, IDR meters are required on any of the following locations/sites:

(a)	All-Inclusive Generation Resources (with the exception of those excluded in this Section);

(b)	Resources bidding into the Ancillary Services Market;

(c)	NOIE metering points used to determine NOIE total Load;

(d)	Service Delivery Points connected to the transmission system (>60KV); and,

(e)	Locations meeting IDR Requirements defined in Section 18, Load Profiling.

10.9.1	ERCOT-Polled Settlement Meters

(1)	The TSP or DSP for EPS meters shall ensure that the EPS Metering Facilities comply with this Section and the SMOG.

(2)	IDR meters used for settlement of EPS Metering Facilities shall:

(a)	Capture energy consumption and/or production in increments consistent with ERCOT defined Settlement Interval;

(b)	Be able to capture energy in increments of five minutes (excluding memory allocation) for new and replacement IDR meters used for settlement;

(c)	Provide interval data for daily polling on a schedule that supports ERCOT’s requirements (typically a daily cycle);

(d)	Be capable of having data retrieved via telemetry by MDAS;

(e)	Have battery or other energy-storage back-up to maintain time during power outages;

(f)	Have remote time synchronization capability compatible with the MDAS;

(g)	Maintain meter clocks on a time reference standard that enables ERCOT MDAS to maintain the IDR data on the Central Prevailing Time.  The meter clock shall be synchronized to within +/- one percent (1%) of the Settlement Interval when compared with the National Institute of Standards and Technology (NIST) Atomic Clock.  ERCOT shall perform the time synchronization for meters at the time of the interrogation if the meter is outside tolerance; and,

(h)	Divide each hour into Settlement Intervals ending as follows:

XX:15:00

XX:30:00

XX:45:00

XX:00:00

10.9.2	TSP or DSP Metered Entities

IDR meters used for settlement of TSP or DSP Metered Entities shall:

(a)	Capture energy consumption in increments consistent with, or in fractions of, ERCOT-defined settlement time interval;

(b)	Provide interval data on a schedule that supports the requirements of final settlement;

(c)	Have battery or other energy-storage back-up to maintain time during power outages;

(d)	Have time synchronization capability;

(e)	Maintain meter clocks on a time reference that enables the TSP or DSP to submit data on the Central Prevailing Time.  The meter clock shall be synchronized to within at least +/- 5% of the Settlement Interval when compared to the National Institute of Standards and Technology (NIST) Atomic Clock;

(f)	Have data aggregated to the appropriate Settlement Interval time block by the TSP or DSP prior to the data being sent to ERCOT if recorded at increments less than the ERCOT defined settlement interval;

(g)	Be able to capture energy in increments of five minutes (excluding memory allocation) for new and replacement IDR meters used for settlement;

(h)	Divide each hour into Settlement Intervals ending as follows:

XX:15:00

XX:30:00

XX:45:00

XX:00:00

(i)	IDR data submitted to ERCOT for Operating Days January 1, 2003, or later must contain only whole days with start times beginning at 0000 and stop times ending at 2359.

10.9.3	Failure to Comply with Standards

If the TSP or DSP fails to comply with the standards for EPS Metering Facilities referred to in this Section and the SMOG, then ERCOT shall notify the PUCT or the appropriate Governmental Authority.

10.10	Security of Meter Data

10.10.1	EPS Meters

(1)	A TSP or DSP is responsible for data security of the EPS Metering Facilities on their system.  This responsibility extends to third-party contracts and access to EPS Metering Facilities.

(2)	A TSP, DSP or any Entity authorized to poll EPS Meters may not issue any EPS Meter programming passwords to any Market Participant.

10.10.1.1	TSP and DSP Data Security Responsibilities

Each TSP and DSP shall:

(a)	Maintain and modify the passwords for programming and read access to EPS Meters;

(b)	Provide the appropriate password access to ERCOT, which will allow ERCOT to synchronize the meter clock;

(c)	Establish any other security requirements for accessing the EPS Meters so as to ensure the security of those meters and their meter data;

(d)	Coordinate any EPS Meter programming parameter changes with ERCOT according to this Section, including informing the Load or Resource Entity of any changes to the meter;

(e)	Upon request of the Resource Entity that represents an EPS metered facility, provide the EPS meter “read only” password to such Resource Entity for such facility and other EPS metered facility required to calculate their QSE Load, to the extent that such provision does not violate the Customer service and protection provisions of the PUCT Substantive Rules; and

(f)	Modify the “read only” password for EPS meters when a Resource Entity that represents a facility requests a change due to data security reasons, provided that such modification does not violate the Customer service and protection provisions of the PUCT Substantive Rules.

10.10.1.2	ERCOT Data Security Responsibilities

ERCOT may request that TSP or DSP alter the password and other requirements for accessing EPS Meters, as it deems necessary.

10.10.1.3	Resource Entity Data Security Responsibilities

A Resource Entity must request that the TSP or DSP modify the EPS Meter “read only” password for a facility when the Resource Entity relationships that affect EPS Meter data security change.  Such request must include the reason for the request.

10.10.1.4	Third Party Access Withdrawn

If, in the reasonable opinion of ERCOT, access granted to a third party interferes with or impedes ERCOT’s ability to poll any EPS Meter, ERCOT may require immediate withdrawal of any access granted to such third party.  Separate access through additional communications ports may be allowed so long as it does not interfere with ERCOT’s ability to communicate with the meter.

10.10.1.5	Meter Site Security

(1)	EPS Metering Facilities and secondary devices that could have any impact on the performance of the EPS Metering Facilities must be sealed to the extent practicable.

(2)	ERCOT shall provide each TSP and DSP with uniquely numbered seals to be used by the TSP or DSP EPS Meter Inspector to seal EPS Meters and EPS Meter test switches.  Procedures for seal use shall be in accordance with this Section and the SMOG.

10.10.2	TSP or DSP Metered Entities

Security for TSP and DSP polled meters and meter data shall be the responsibility of the TSP or DSP. Each TSP and DSP shall maintain polled meters in accordance with applicable Governmental Authority rules and regulations.  The TSP and DSP shall ensure that only Customer-approved Market Participants have access to the Customer meter.

10.11	Validating, Editing, and Estimating of Meter Data

10.11.1	EPS Meters

The raw meter data that ERCOT retrieves from EPS Meters must be processed by MDAS using the Validating, Editing, and Estimating (VEE) procedures published in Section 11, Data Acquisition and Aggregation, and the SMOG in order to produce Settlement Quality Meter Data. During periods for which no primary EPS Meter data is available, ERCOT shall use the backup meter data or substitute estimated usage data for that metered Entity using estimation procedures referred to in these Protocols and the SMOG.  This data shall be used by ERCOT in its settlement and billing process.

10.11.2	Obligation to Assist

At the request of ERCOT, a TSP, DSP and Market Participant shall promptly assist ERCOT in correcting or replacing defective data from EPS Meters and in detecting and correcting underlying causes for such defects.  Such assistance shall be rendered in a timely manner so that the settlement process is not delayed.

10.11.3	TSP or DSP Settlement Meters

(1)	The TSP and DSP shall provide ERCOT with Settlement Quality Meter Data for the TSP or DSP Settlement Meters on its system and shall ensure that at a minimum the VEE requirements as specified in the Uniform Business Practices (UBP) standard for Validating, Editing, and Estimating have been properly performed on such data.  ERCOT shall not perform any VEE on the Settlement Quality Meter Data it receives from TSP or DSP.

(2)	The following UBP manual validation processes are exempt for Interval Data:

(a)	Spike Check; and

(b)	Reactive channel check for kWh data

10.12	Communications

10.12.1	ERCOT Acquisition of Meter Data

ERCOT shall acquire meter data via the following communication links:

(a)	ERCOT private communication network established by ERCOT for ERCOT Real-Time metered Entities; and

(b)	Standard voice telephone circuit or other ERCOT-approved communication technology provided by the TSP or DSP for EPS Meters.

10.12.2	TSP or DSP Meter Data Submittal to ERCOT

TSP and DSPs shall submit meter consumption data to ERCOT through a standard data interface into the MDAS.  In order to submit meter consumption data, a TSP or DSP shall use an automated system with an ERCOT-approved and tested interface to MDAS.

10.12.3	ERCOT Distribution of Settlement Meter Data

ERCOT shall distribute Settlement Quality Meter Data to Market Participants:

(a)	Whenever a TSP or DSP submits meter consumption data to ERCOT, information pertaining to specific Market Participants shall be removed and automatically forwarded on to that specific Market Participant (i.e., a CR will automatically receive the meter consumption data and other information for the ESI IDs that the CR represented during the meter data timeframe.); and

(b)	On Request – An Market Participant may submit an electronic request via the MIS Certified Area for specific meter consumption data.  ERCOT will receive and validate the request and, if appropriate, automatically forward the appropriate information to the Market Participant.

10.13	Meter Identification

The device id used to identify an EPS Meter shall be unique for such meters on the ERCOT System.  ERCOT shall maintain a master list of device ids and shall notify each TSP and DSP if the device id selected has been used elsewhere in MDAS.

10.14	Exemptions from Compliance to Metering Protocols

10.14.1	Authority to Grant Exemptions

ERCOT may grant on a case by case basis, exemptions from compliance on a temporary basis until new arrangements can be completed in accordance with the guidelines as listed below.  Any permanent exemption to this Section requires approval by the Technical Advisory Committee (TAC) and the ERCOT Board.  Any permanent exemption shall be subject to periodic review and revocation by the ERCOT Board.

10.14.2	Guidelines for Granting Temporary Exemptions

ERCOT shall use the following process when considering applications for temporary exemptions from compliance with this Section and the SMOG.

(a)	Publication of Guidelines:  ERCOT shall post on the MIS Public Area the general guidelines that it will use when considering applications for exemptions within five Business Days of a change of guidelines, so as to achieve consistency in its reasoning and decision-making and to give prospective applicants an indication of whether an application for exemption may be considered favorably.

(b)	Publication of Decision:  ERCOT shall post on the MIS Public Area the application for exemption and whether the application was approved or rejected by ERCOT and the reasons for rejecting the application, if applicable, on a quarterly basis.

10.14.3	Procedure for Applying for Exemptions

(1)	All applications to ERCOT for exemptions from compliance with the requirements of this Section must be submitted in writing.  ERCOT shall confirm receipt of an application within three Business Days of receipt.  For temporary exemptions, ERCOT shall decide whether to grant or reject the exemption within 45 Business Days of receipt.  For permanent exemptions, ERCOT shall forward the application to TAC for review at the next scheduled meeting for which appropriate Notice can be made.  At any time during the application process, ERCOT may require the applicant to provide additional information in support of its application.

(2)	The applicant shall provide such additional information to ERCOT within five Business Days of receiving the request or within such other period as ERCOT may specify.  If ERCOT requests additional information more than 40 Business Days after the date on which it received the application, ERCOT shall have an additional seven  Business Days after receiving that additional information in which to consider the application.  If the applicant does not provide the additional information requested, then ERCOT shall reject the application, in which case it will notify the applicant that its application has been rejected for failure to provide the additional information.

10.14.3.1	Information to be Included in the Application

The application for exemption to ERCOT shall include:

(a)	A detailed description of the exemption sought. including specific reference to the relevant Section(s) of these Protocols or the SMOG authorizing ERCOT to grant the exemption, and the Metering Facilities to which the exemption will apply;

(b)	A detailed statement of the reason for seeking the exemption, including any supporting documentation;

(c)	Details of the Entity(s) to which the exemption will apply;

(d)	Details of the location to which the exemption will apply;

(e)	Details of the period of time for which the exemption will apply, including the proposed start and finish dates of that period; and,

(f)	Any other information requested by ERCOT.