## Slide 1: OOM During Alerts
ERCOT TAC
June 7, 2007
Dan Jones
Potomac Economics

## Slide 2: ERCOT Freq. Desk Procedures Before 3/24/2007
2.6.9 Provide Advanced Notice of Diminishing Responsive Reserve | 
Step # | Procedural Steps
PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves.
NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS
1 | IF Adjusted Responsive Reserve is equal to or less than 3000MW, issue an Advisory. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.”
2 | IF Adjusted Responsive Reserve is equal to or less than 2500MW, issue an Alert. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Alert to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.”
3 | Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability.
3a | Issue dispatch instructions to QSEs to suspend any ongoing generating unit or resource performance testing.
3b | Utilize available resources providing Replacement and Non-Spin Reserve Services that can be deployed to increase Responsive reserves.

## Slide 3: ERCOT Freq. Desk Procedures After 3/24/2007
2.6.9 Provide Advanced Notice of Diminishing Responsive Reserve | 
Step # | Procedural Steps
PURPOSE: | Guidelines for issuing advance notice of diminishing Responsive Reserves.
NOTE: | Adjusted Responsive Reserve (ARR) Reference Display: EMS, Generation Area Status, ADJ_RESPONS
1 | IF Adjusted Responsive Reserve is equal to or less than 3000MW, issue an Advisory. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Advisory to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.”
2 | IF Adjusted Responsive Reserve is equal to or less than 2500MW, issue an Alert. Typical script: “This is the ERCOT system operator. ERCOT is issuing an Alert to provide notice that Adjusted Responsive Reserve has fallen to <state MW amount>. Please keep your Resource Plan updated and notify ERCOT of any changes in your system that will prevent you from meeting your Responsive Reserve obligation.” Implement the following actions: Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability. Issue dispatch instructions to QSEs to suspend any ongoing generating unit or resource performance testing. Deploy Non-Spin and “Quick Start” GTs as follows: Deploy Non-Spin if available.. If Non-Spin is unavailable or if all Non-Spin has been deployed,dispatch to full output as many “Quick Start” GTs as necessary that are bid into the Balancing Market that show “On” and “Plan MW” 0. Deplete these resources before proceeding to c. If all “Quick Start” GTs that were “On” are depleted, OOMC/OOME the remainder of the “Available” “Quick Start” units. Deplete these resources before proceeding to d. If all “Quick Start” units are depleted, OOMC/OOME any additional “Available” units.

## Slide 4: Protocols 5.6.6.2
Prior to declaring EECP Step 1 detailed in Section 5.6.7, EECP Steps, ERCOT shall:
(1) Start RMR units available in the time frame of the emergency. RMR units should be loaded to full capability;
(2) Issue Dispatch Instructions to QSEs to suspend any ongoing ERCOT required generating unit or Resource performance testing;
(3) Utilize available resources providing Non-Spin Reserve Services that can be deployed to increase Responsive Reserves; and
(4) ERCOT shall use the Reserve Discount Factor (RDF) for the purpose of monitoring Physical Responsive Capability (PRC). The PRC will be used by ERCOT to determine the appropriate Emergency Notification and EECP Steps.
In addition, ERCOT may issue an appeal through the public news media for voluntary load reduction if authorized by the ERCOT Chief Executive Officer or its designee based on an evaluation of existing and expected system conditions.

## Slide 5: Protocols 5.6.7
Step 1 — Maintain ERCOT Physical Responsive Capability (PRC) on units plus RRS MW provided from LaaR Equal to 2300 MW.
ERCOT will:
(1) Utilize available DC tie capability that is not already being used by the market;
(2) Notify the Southwest Power Pool Security Coordinator; and
(3) Issue OOM dispatch instructions to uncommitted units available within the expected timeframe of the emergency.
(4) Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers.

## Slide 6: Protocols 6.5.10(4)
ERCOT may use OOMC when necessary to provide ERCOT System security and capacity adequacy. ERCOT will Dispatch Resources for OOMC and OOME Service in such a way as to minimize the use of these services as much as practicable.