## Slide 1: Proposed Change to Methodology regarding Regulation Service
TAC 6/07/2007

## Slide 2: Current Methodology
Divides the Regulation Up and Down requirements into blocks of Hours
Calculates the average and standard deviation of deployed Regulation Up and Down by hour in the previous month and same month of the previous year.
Targets an exhaustion rate of 1.2% or 35 settlement intervals/month

## Slide 3: Proposed Methodology
Removes the requirement to Block Hours for procurement of Regulation Up and Down
Calculates the 98.8 percentile of deployed Regulation Up and Down in the previous month and same month of the previous year by hour
Targets an exhaustion rate of 1.2% or 35 intervals/month
Adds a back-cast requirement that allows ERCOT to adjust when the exhaustion rate exceeds 1.2%.

## Slide 4: Historical Regulation Procurement

## Slide 5: SUMMARY
A 98.8th percentile method using the same historical data with no grouping among hours appears to produce results that are more efficient and closer to the reliability objectives
Utilizing the back-cast in a feedback loop will allow ERCOT to adjust if the exhaustion rate exceeds 1.2%.