## TPTF Comments & Responses
Document Name: | [5 empty] | Integration Design Authority, Joint Owned Unit Modeling Version 0.09
S.No. | Issuing Entity (Name) | Page Number | Section | Req./Table /Fig. | No., Pg, Sec., Req. | Description | Response Type | Reviewer | Reason / Comment
207 | ftrefny | Pg 4 |  |  |  | Inserted Text (Table 1 - Split Generation Resource Modeling in Applications) | Accepted | IDA | The Table 1 is entered one more time later. Duplicate entry is not needed. NSM as a physical model is suggested by ABB to be more efficient to implement. Outage Scheduler should use physical model of the generator.
208 | ftrefny | Pg 5 |  |  |  | Delete Text Sectionj 4.JOU Optimization Model | Accepted | IDA | This Section is related to implementation aspects. Especially, implementation of CCP SGRs is problematic from implementation point of view, if it is possible at all to implement it with practically acceptable performances of solution process
9 | guermouches | Pg 2 |  |  |  | Inserted Text ((This paragraph suggests that unit registration parameters have to be coordinated in some fashion) ) | Clarification Provided | IDA | Yes, parameteers for SGRs must be consistent with physical characteristics of JOU. This is as par protocol.
11 | guermouches | Pg 2 |  |  |  | Inserted Text ( (this is not clear. What is meant by online? Is this in reference to outages and maintenance? Or selected offer? What about configuration of units such as CC?) | Clarification Provided | IDA | This applies to all: outages, maintenance, selected offers, Each share of CCP must be in the same configuration all the time.
14 | guermouches | Pg 2 |  |  |  | Inserted Text ( (Then it cannot be an independent offer this statement is self contradicting)) | Clarification Provided | IDA | The offers are independent, but the decision whether they will be awarded is coordinated due to physical constraint (have to commit the whole unit). QSE submits three part energy offer for each SGR independently. Submitted offers can be selected together, no other way is possible. Please see the Nodal Protocol.
16 | guermouches | Pg 2 |  |  |  | Inserted Text ( This paragraph contradicts the previous paragraph. If SGR are modeled as separate resources then their would be no need to jointly commit or decommit the resource. The problem is that the language in this paragraph lacks precision: it allows for an action and its opposite (contra) to occur at the same time making the whole statement both permissible and impermissible at the same time. Sort of both true and false.) | Accepted | IDA | The SGRs MUST be committed/decommitted together. Document updated.
18 | guermouches | Pg 2 |  |  |  | Inserted Text ( . [Comment: Allocating EPS Metered Data to Generator Virtual Meters (Section 10.3.2.1.2) gives an example of steady state operation of a joint unit where the output is split based on percentage ratios. There is not an example of the unit being ramped up or down when the energy bids of one joint owner may be selected while the energy bids of another joint owner may not be selected. The generation % ratios sent to ERCOT would then represent the energy bids selected by ERCOT not the % ownership in the unit. The generation % ratio sent to ERCOT when not all of the SGR energy bids are selected needs to be worked out between the owners of the plant. | Clarification Provided | IDA | This is the Nodal Protocol requirement. The paper points to a protocol section. There is no new proposal.
19 |  | Pg 2 |  |  |  | Example: If the JOU were at full load and then was backed off 50 MW the 50 MW reduction may be allocated to only one QSE that had the highest energy bid. The generation % ratios would then be based on the energy bids that were accepted by ERCOT.]) | Clarification Provided | IDA | This suggestion requires changes of the Nodal Protocol.
21 | guermouches | Pg 3 |  |  |  | Inserted Text ( (This is an incomplete sentence is this the view of the author? A factual statement or both? or is it intended to say the protocols require modeling of each SGR but the reality is…)) | Clarification Provided | IDA | According to the Nodal Protocol all input data and output results should be represented on individual SGR basis. The rest of this statement points to implementation of optimal processing of JOU/SGRs. The term “internal representation” refers to mathematical modeling within market Applications.
22 | guermouches | Pg 3 |  |  |  | Inserted Text ( (What is this?)) | Clarification Provided | IDA | This statement is based on Nodal Protocol requirement to register physical JOU and all its SGRs as separate generation resources.
25 | guermouches | Pg 3 |  |  |  | Inserted Text ( HOW?) | Clarification Provided | IDA | In the same way as for any other generating resource.
28 | guermouches | Pg 4 |  |  |  | Inserted Text ( What is a transition time point? Do you mean time to startup? ) |  | IDA | The transition time is cooling time at which generating unit changes state hot-to-intermediate and intermediate-to-could.
29 | guermouches | Pg 4 |  |  |  | Inserted Text ( You do not mean to have duplication of JOU?? How would the NMMS be useful this way? What representation are we talking about here? Or do you mean this representation is restricted to EMMS (2 models JOU and SGR for EMMS purposes)) | Clarification Provided | IDA | Yes, NMMS network should include both JOU and SGRs. The Market Applications will optimize SGRs, while Network Applications will analyze JOU.
31 | guermouches | Pg 4 |  |  |  | Inserted Text ( That is ok in the first paragraph in 3 the word BOTH is misleading it could be mean to say hat both…at the same time.) | Clarification Provided | IDA | Yes, both JOU and SGRs will be represented in network model within NMMS. At least the registration data for both JOU and SGRs should be within NMMS.
32 | guermouches | Pg 5 |  |  |  | Inserted Text ( The graphs below assume the same QSE is representing the JOU when in fact you may have multiple QSE.) | Clarification Provided | IDA | Yes, can be more than two SGRs, but here are illustrated only two. There is master QSE “representing” JOU, and separate QSE representing individual QSE.
33 | guermouches | Pg 6 |  |  |  | Inserted Text ( (only if you insist on the validation steps)) |  | IDA | This can be deleted.
35 | WoodardS | Pg 6 |  |  |  | Inserted Text ( . [Comment: The above paragraph needs to be rewritten to clarify the meaning.]) | Accepted | IDA | The Nodal Protocol dictate completely separate offer submission, processing and settlement for each SGR.
36 | WoodardS | Pg 6 |  |  |  | Inserted Text ( (IT HAS TO BE SEPARATE BINARY VARIABLE NOT COMMON). THESE additional constraints need to be discussed for example the trigger of one binary to one would have to set the others to 1.) | Accepted | IDA | All SGRs oh the same JOU MUST be committed/decommitted together. Here is suggested to use common binary variable instead of separate binary variables and additional tightening constraints to reduce number of variables and number of constraints. Of course, the optimal solution must be the same.
37 | guermouches | Pg 6,7 |  |  |  | Inserted Text ( This is not be needed if ERCOT ensures that the data consistency is performed on a regular basis. The JOU QSE will submit data that is reviewed by ERCOT to ensure that the “physical” parameters are identical for all QSE. When performing the optimization the model would check for consistency if inconsistency is detected it will resort to last data filed at ERCOT.) | Accepted | IDA | Agreed. This is just suggestion how to implement required functionality.
39 | guermouches | Pg 7 |  |  |  | Inserted Text (. The sub-optimal JOU scheduling is caused by having each JOU co-owner provide separate independent bids. This modeling problem will have to be accepted as a result of splitting the JOU into several independent pieces.) But this should not be ERCOT concern. | Clarification Provided | IDA | The point here is: JOU splitting enforces approximation that result in sub-optimal solution. This solution is not the best for individual SGRs, whole JOU nor overall system.
41 | guermouches | Pg 7 |  |  |  | Inserted Text ( [THIS SHOULD HAVE BEEN PROPOSED ABOVE AND NOT WAIT TILL HERE TOWARD THE END OF THIS DOCUMENT}) | Clarification Provided | IDA | This is proposed here because this is relevant for implementation only. The integrate JOU model is built internally using SGR data submitted by QSE.
45 | guermouches | Pg 8 |  |  |  | Inserted Text ( THIS STILL IS A PROBLEM. IT WILL NOT SELECT A UNIT IF THE STARTUP COST FROM SOME OWNER PER SOME OFFER IS HIGH. YOU COULD JUST AS EASILY SET A RULE THAT STATES THE STARTUP COST SHOULD BE THE MINIMUM OF ALL STARTUPS. OR: REQUIRE A COMMON STARTUP OFFER FOR JOU THIS OFFER COULD BE PERIODICALLY UPDATED) |  | IDA | This comment requires change of the Nodal protocol. It will be good idea that master QSE submits all non-sharable JOU parameters that apply to all SGRs, like startup costs, minimum energy costs, min up/down time, …
47 | guermouches | Pg 9 |  |  |  | Inserted Text ( (BUT THAT SHOULD NOT BE A CONCERN TO ERCOT)) | Clarification Provided | IDA | NOTED.
48 | guermouches | Pg 10 |  |  |  | Inserted Text ( [Comment: ERCOT should verify that JOU parameters that need to be the same for all JOU co-owners are consistent either with a) values that need to be the same are the same or b) values that are based on percentage of ownership add up to the total percentage.]) | Accepted | IDA
57 | WoodardS | Pg 10 |  |  |  | Inserted Text ([Comment: It might be better to have one value input for the following generation characteristics and have the value split by ownership as shown below: JOU parameter JOU QSE1 QES2 Ramp Rate (MW/min) 4 40% 30% Min Run Time (Hours) 24 100% 100% Min Down Time (Hours) 8 100% 100% 1 | Clarification Provided | IDA | This comment requires changes of the Nodal Protocol.
58 | ERCOT | Pg 8 |  |  |  | Inserted Text (Section 3.8 (7) states that each QSE that represents a SGR will submit verifiable cost only for the portion they own. For SGRs that do not have verifiable costs submitted yet ERCOT will use Resource Category Generic Startup Cost for start up offer caps and make-whole payment. RCGSC is listed in Protocols as dollars per start per resource category. ERCOT needs direction on methodology and data to be used to split RCGSC for SGRs.) | Accepted | IDA | For SGR's that do not have verifiable costs, ERCOT shall split the RCGSC across the owners based on the percentage ownership indicated in the GARF. A modification to the Nodal Protocls is probably necessary to make this clear.
63 | GP&L | Pg 3 |  |  |  | Inserted Text (GP&L Question: Please explain how these are used – for instance how are you going to RUC a SGR separately??) | Clarification Provided | IDA | They are used in the same way as proxy energy curves for any other generating resource RUC will be constrained to commit and decommit all SGRs together.
64 | GP&L | Pg 3 |  |  |  | Inserted Text (GP&L Question: What happens when in “real time” there is a temporary limitation that derates the minimum or maximum and all of the SGR owners do not adjust to the limits accordingly – for example 1 SGR does not adjust to the limit??? Are you checking against the registered value that is modified in real time via the MMS web service displays for modifying registered values) | Accepted | IDA | This is handled just like any other (non-jointly owned ) unit. HSL is checked against a reasonability limit and alarmed nad possibly clamped if limit is violated. The answer is Yes.
66 | GP&L | Pg 3 |  |  |  | Inserted Text (GP&L Question: What happens when in “real time” there is a temporary limitation that derates the ramp rate and all of the SGR owners do not adjust the ramp rate accordingly – for example 1 SGR does not adjust to the new ramp rate??? Are you checking against the registered value that is modified in real time via the MMS web service displays for modifying registered values) | Clarification Provided* | IDA | Just as with for any other unit regisred ramp rate is used.
68 | GP&L | Pg 9 |  |  |  | Inserted Text (GP&L Comment: Please explain in more detail the sentences in yellow above:) | Clarification Provided* | IDA | .The “integrate JOU model “ is explained in Section 4. Here is just summary related to implementation of this approach. It is especially relevant for CCP JOU, what is very problematic from implementation point of view, if it is possible to implement it at all!
69 | GGraham | Pg 2 |  |  |  | Inserted Text ( (Does this mean “identical” or just feasible?)) | Clarification Provided* | IDA | As it is required by the Nodal protocol and stated in the paper "the capacity limits and ramp rates submitted for individual SGRs must be consistent with JOU physical capabilities", i.e sum of SGR capacities and ramp artes must be equal to JOU capacity and ramp rate.
70 | GGraham | Pg 2 |  |  |  | Inserted Text ((Requires consensus between JOU partners)) | Clarification Provided | IDA | These are Nodal protocol requirements.
71 | GGraham | Pg 2 |  |  |  | Inserted Text (Does it matter if one JOU is Dynamically Scheduled and the other one(s) are not? What if one JOU is Self Committed and the other JOU submits a 3 part offer?) | Clarification Provided | IDA | If one SGR is dynamically scheduled, the other must be self commited and can submit energy offers. But, the SGR can not be self-committed independently, only whole JOU can be self committed, i.e. all SGRs should be self committed.
72 | GGraham | Pg 3 |  |  |  | Inserted Text ( So JOU entities may have different verifiable costs for their portion of the same unit?) | Clarification Provided | IDA | Yes, according to the Nodal Protocol SGRs represent independent generating resources
73 | GGraham | Pg 3 |  |  |  | Inserted Text ( Again – Requires consensus between JOU entities.) | Clarification Provided | IDA | SGRs must be shares of physical JOU. Otherwise, overall system operation becomes physically infeasible.
74 | GGraham | Pg 3 |  |  |  | Inserted Text (What about Voltage Control Responsibility (ie. Master QSE responsibilities) Reactive Testing Full Load testing etc.?) | Clarification Provided | IDA | Please see above statement “the voltage stability and control studies should used physical model of JOU generation facility”

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.