| NOGRR Number |  | NOGRR Title | Nodal Operating Guides - Section 8 - Attachment I, Security, Facilities, and Connectivity Requirements of WAN Systems |
| --- | --- | --- | --- |
| Date Posted |  |  |  |
| Nodal Operating Guide Section(s) Requiring Revision (Include Section No. and Title) |  | Section 8 - Attachment I, Security, Facilities, and Connectivity Requirements of WAN Systems |  |
| Requested Resolution (Normal or Urgent, and justification for Urgent status) |  | Normal |  |
| Revision Description |  |  |  |
| Reason for Revision |  |  |  |
| Overall Market Benefit |  |  |  |
| Overall Market Impact |  |  |  |
| Consumer Impact |  |  |  |
| Credit Implications (Yes or No, and summary of impact) |  |  |  |
| TPTF Review (Yes or No, and summary of conclusion) |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Stephen C. Knapp on behalf of the Operating Guides Revision Task Force (OGRTF) |
| E-mail Address | Steve.knapp@constellation.com |
| Company | Constellation Energy Commodities Group, Inc. |
| Company Address | 111 Market Place, Suite 500, Baltimore, Maryland 21202 |
| Phone Number | 410-468-3606 (Office) / 443-286-6785 (Cell Phone) |
| Cell Number | 410-468-3419 |
| Market Segment |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive NOGRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the NOGRR.

| Assumptions | 1 | Example: Key assumptions used in estimating market cost and/or benefit |  |
| --- | --- | --- | --- |
|  | 2 | Ex: Dependencies on other projects or other timing requirements |  |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | Example: Cost per MP to implement | Example: $10,000 each for 50 QSEs |
|  | 2 | Ex: Add’l staff required per MP | Ex: 1.5 FTE each for 6 TDSPs @ $65/hour |
|  | 3 |  |  |
|  | 4 |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Example: Reduced MP costs | Example: 2 FTE reduction for 25 CRs @ $65/hour |
|  | 2 | Ex: Enhanced MP efficiency | Ex: 2 hour savings per day for 50 generators @$65 |
|  | 3 | Ex: Reduced congestion cost | Ex: 0.5% reduction in total congestion cost |
|  | 4 |  |  |
| Additional Qualitative Information | 1 | What to include here: Benefits that are difficult to quantify |  |
|  | 2 | What to include here: Benefits that are not certain but relatively likely |  |
|  | 3 | What to include here: Customer service impacts, cash flow impacts, transaction speed, etc. |  |
|  | 4 |  |  |
| Other Comments | 1 | What to include here: Thoughts on ERCOT systems impacts |  |
|  | 2 | What to include here: Potential manual workarounds or delivery options |  |
|  | 3 | What to include here: Other comments of value to PRS, TAC and the Board of Directors |  |
|  | 4 |  |  |

Proposed Nodal Operating Guide Language Revision

ERCOT Operating Guides

Section 8

Attachment I

Security, Facilities, and Connectivity Requirements of WAN Systems

DRAFT

(Effective Upon Texas Nodal Market Implementation)

A QSE or TSP involved in the transfer of the critical data identified in Attachment 8A of this guide, will be required to provide the following communication resources to support the connection to the ERCOT private network:

(a)	Provide an analog business phone line or PBX analog extension for trouble-shooting and maintenance of equipment;

(b)	Provide a height of 24” of rack space in a 19” wide rack;

(c)	Provide two separate UPS single-phase 115 VAC 20 amp circuits, each with 4 receptacles in the 19” rack listed above;

(d)	Provide building wiring from circuit termination to equipment rack;

(e)	Within 24-hours notice, provide ERCOT employees or contractors access to the communication facility;

(f)	Within 1-hour notice, provide emergency access to the facility to ERCOT employees or contractors;

(g)	Provide on site personnel to escort ERCOT employees or contractors;

(h)	Provide a Firewall or router, located at the Market Participant site, for the network address translation of internal Market Participant addresses to external addresses on the ERCOT LAN;

(i)	Market Participant will be required to sign a security connection agreement with ERCOT;

(j)	Provide connectivity from Market Participant Firewall or Router to ERCOT LAN located at Market Participant site. Market Participants are responsible for their own security through this connection;

(k)	Provide a channel bank with at least one T1 interface, 4 FXS and two 4 wire analog ports. Connect FXS (e.g. PBX, key system) and 4 wire ports to the appropriate equipment.  On the digital T1 stream, levels for voice are zero dpm for transmit and receive;

(l)	Hotline must be a 500 set not attached to the Market Participant’s Phone System;

(m)	Dual cable entrances to Market Participant, connecting to different Telco Central Offices highly recommended; and

(n)	Provide ERCOT with internal IP addressing scheme as needed for network design. This will be kept confidential.