## Slide 1: Black Start Study
Verification Of Synchronization Ability

## Slide 2: Justification
1) Each contracted black Start Unit has a set of physical test is it must pass over a period of 6 years
  Basic Start-up – each time awarded the bid
  Line energization – every three (3) years
  Load pickup – every six (6) years
  Start the next start unit or the next start unit’s largest motor – once unless the next start unit changes
  2) ERCOT has an automated process to pick the contracted units with a specific set of criteria
  3) NERC Standard EOP-005-1 R7 states “Each Transmission Operator and balancing Authority shall verify the restoration procedure by actual testing or by simulation”.

## Slide 3: Justification cont.
4) There currently is no criteria in ERCOT for an actual or simulation test of establishing and stabilizing a black start island and the synchronization of two or more Black Start Islands.
5) The Black Start Task Force (BSTF) has pursued this from the perspective of synchronizing two islands will provide the assumption that most if not all islands can be synchronized.
6) The BSTF estimates that a ball park cost to accomplish this study will be on the order of $180,000 for a two island study.

## Slide 4: Request
ROS requests that TAC support the BSTF effort through the 2008 ERCOT budget to verify the ability of ERCOT to build, stabilize and synchronize two Black Start Islands.