ERCOT OPERATIONS REPORT

ON THE

EECP EVENT

OF

June 09, 2007

Executive Summary	3

Time Line and Description of Significant Events	4

Observations/Data Review...........................................................................................5

Lessons Learned.........................................................................................................12

### Executive Summary

ERCOT implemented Step One of its Emergency Electric Curtailment Plan (EECP) on

June 09, 2007.  Factors that led to ERCOT implementing the EECP Step One:

At 09:34:00 an Advisory was issued for Adjusted Responsive Reserve (ARR) below 3000 MW.

At 11:16:00, ERCOT declared an Alert for ARR below 2500 MW.

At 11:24:00 as ARR declined, ERCOT declared EECP step 1.  The Total ERCOT Telemetered SCE was -610 MW at this time.

At 11:30:00 Quick Start CTs and RMR Units instructed to go to the top.

The lowest telemetered SCE point during the EECP was -830 MW at 11:45:20.

Day-Ahead Load Forecast for June 9th planned for hour ending 11 One-Hour Average Load of 39,648 MW.  However the indicated real-time load was 41,426 MW.  This is a difference of 1778 MW of unexpected load.  Hour-Ending 12 One-Hour Average was 42,443 MW; real time load was 44,481 MW.  (A difference of 2038 MW)  This is a discrepancy of 4.58%.

The RPRS study for the Operating Day of June 9th, 2007 did not see the need to procure generation for capacity needs Day-Ahead.  The total on-line capacity at 11:00 in the RPRS market study was 46,845 MW; the actual on-line system capacity in real-time was 46,074 MW, a 771 MW difference.  There were no non-spin requirements.

As ARR recovered, EECP was terminated at 12:10.

Time Line and Description of Significant Events

- 09:34 Advisory Issued due to ARR below 3000 MW.  Actual ARR was at 2954 MW.

- 09:34 ERCOT requested SCE information from QSE B.

- 09:42 ERCOT requested SCE information from QSE C.

- 11:16 Alert issued due to ARR below 2500 MW.  Actual ARR was at 2432 MW.

- 11:23 ARR dropped below 2300 MW to 2287 MW. (7 minutes from when alert was issued)

- 11:24 Implemented EECP 1 due to ARR at 2287 MW.

- 11:26   Inquired QSE B about SCE hanging out at -426 MW.  QSE reported a unit issue and expected problems until interval ending 13:00. (SCE had been hanging out since 10:00.)

- 11:29 – 11:46 Several QSEs called to inform ERCOT of additional available resources and start times if needed.

- 11:30 1065 MW of quick start CTs ordered to start.  Also requested RMR Units to the top.

- 11:32 ARR rose above 2300 MW to 2309 MW.

- 11:45 ARR rose above 2500 MW to 2516 MW.

- 11:51 Notified SPP that at 11:24 ERCOT implemented EEA Alert 1 (EECP Step 1) due to ARR below 2300 MW.  Per shift supervisor ERCOT was not requesting Emergency Power.  Anticipating EEA Alert 1 would be canceled as soon as quick start units were on.  Quick start units have been ordered.  ARR was 2715 MW.

- 12:10 Terminated EECP 1. Alert still in effect. ARR at 2965 MW.

- 12:24 Notified SPP EEA Alert 1 was cancelled at 12:10.

- 20:00 Alert for ARR below 2500 MW was cancelled.  ARR was at 3434 MW.

- 21:30 Advisory for ARR below 3000 MW was cancelled.  ARR was at 3365 MW.

Observations/Data Review

6/9/07 09:00 – 13:00 ARR, RRS, AND LOAD

09:00 – 13:00 1-HOUR-AVERAGE DAY-AHEAD LOAD FORECAST

AND 1-HOUR-AVERAGE REALTIME LOAD

09:00 – 13:00 HOURLY DAY-AHEAD RPRS CAPACITY VS.

HOURLY REAL-TIME CAPACITY

09:00 – 13:00 ARR, RRS, AND TOTAL SCE

11:00 – 12:00 LOAD AND SCE

09:00 – 13:00 FREQUENCY AND REGULATION

09:00 – 13:00 QUICK START CTs

Lessons Learned

- No observed deviations from ERCOT established procedures.

- Advisories do not seem to prompt action from QSE.

- The ARR diminished so quickly from the Alert to the EECP trigger point that ERCOT was not able to call or deploy the quick start CTs prior to EECP.