## Slide 1: ROS Report to TAC
Stuart Nelson
June 7, 2007

## Slide 2: General Topics
No EECP Events
Compliance Review Process Update
Support Ancillary Services Study
Long Term Solutions Task Force

## Slide 3: Regional Reliability Standards
ROS will review process to setup Standards Drafting Teams
Four potential Regional Standards (“NERC fill in the blank standards”)
ROS felt that the ERCOT Board should set direction for SCR procedural review

## Slide 4: Nodal Guide Conversion
OWG comment period ends June 29
OGRTF will address OWG comments
Nodal Guides posted for comment period in July 2007
Publish Nodal Guides by August 2007
ROS approval at September 2007 meeting
TAC approval at October 2007 meeting

## Slide 5: Black Start Study – Background
Each contracted black Start Unit has a set of physical test is it must pass over a period of 6 years
  Basic Start-up – each time awarded the bid
  Line energization – every three (3) years
  Load pickup – every six (6) years
  Start the next start unit or the next start unit’s largest motor – once unless the next start unit changes
ERCOT has an automated process to pick the contracted units with a specific set of criteria
NERC Standard EOP-005-1 R7 states “Each Transmission Operator and balancing Authority shall verify the restoration procedure by actual testing or by simulation”

## Slide 6: Black Start Study – Background
No ERCOT criteria to test or simulate synchronization of multiple black start islands
BSTF believes that the plan can be verified through a study syncronizing 2 islands
Estimated study cost - $180,000

## Slide 7: ROS Request
ROS requests that TAC support the BSTF effort by budgeting for a study in 2008 to verify the ability of ERCOT to build, stabilize and synchronize two black start islands.

## Slide 8: Questions
?