- Bell County East – TNP One

- 345 kV Line Construction

- TXU Electric Delivery Transmission Grid Planning

- November 30, 2006

(Revised February 2, 2007)

- BELL COUNTY EAST – TNP ONE 345 kV LINE

- CONSTRUCTION PROJECT

- Introduction

This report documents the need for the proposed construction of the 40 mile Bell County East – TNP One 345 kV line which will be a double-circuit steel lattice tower line that will be constructed using 2-1590 kcmil ACSR conductor (2730 Amperes per circuit). Also, the Bell County East 345 kV Switching Station (breaker and half) which will be located approximately 10 miles southeast of Temple Sw Sta in the Temple Sw Sta – Sandow 345 kV double-circuit line will need to be constructed.   See Appendix for an area map and one-line.

Existing generation at TNP One Plant (306 MW) is connected radially to Twin Oak Switching Station by an 18.1-mile double-circuit 345 kV line that uses a conductor rated at 2775 Amperes for each circuit.  In 2009 the proposed Oak Grove Plant (1710 MW net) located at Twin Oak Switching Station will begin commercial operation.   There are three paths from Twin Oak Switching Station for this generation and the TNP One Plant to exit the area.  The Twin Oak – Jewett 345 kV circuit is on a double-circuit lattice tower line that uses 2-1590 kcmil ACSR conductor operating up to 90º C and is approximately 35.8 miles long.  The Twin Oak – Gibbons  and Twin Oak – Jack Creek 345 kV circuits are on a double-circuit lattice tower line that uses 2-1590 kcmil ACSR conductor operating up to 90º C and are approximately 48 and 18 miles long, respectively.   The Twin Oak – Limestone 345 kV circuits are on a double-circuit lattice tower line that uses 2-1590 kcmil ACSR conductor operating up to 90º C and is approximately 23.5 miles long.  In 2009, the Sandow 5 Plant (581 MW net) will become operational.  This replaces Sandow Units 1, 2, 3 (360 MW of generation) that were retired in 2006.   In 2011, the Sandy Creek Plant (925 MW net) will be operational and it will be located at the proposed Rattlesnake Road Switching Station which will be located about 1.5 miles east of Lake Creek on the Lake Creek to Jewett 345 kV line.  The existing 1.5 mile 345 kV line section between Lake Creek and Rattlesnake Road Sw Sta will be upgraded from 2-795 kcmil ACSR conductor to 2-959.6 kcmil ACSS/TW conductor (designed to operate up to 180º C to obtain 3200 amperes of capacity) when Sandy Creek becomes operational.

The addition of the Oak Grove, Sandy Creek, and Sandow 5 Plants increase the need for additional north – south transfer capacity.  Contingencies involving the Tradinghouse – Lake Creek – Temple corridor restrict transfer levels on the west corridor because they force increased power onto the parallel 138 kV system resulting in overloads.   The construction of a 345 kV double-circuit line from Bell County East – TNP One would alleviate these overloads by providing a 345 kV path around this bottleneck.   Additionally, the TNP One to Bell County East double circuit 345 kV line will add another exit for the Oak Grove and TNP One generation, and will provide a second and separate transmission line to TNP One.   This will relieve some of the pressure on the 345 kV lines into Houston from the north reducing or eliminating contingency overloads on parallel paths into the Houston area.  Completing the proposed 345 kV line will add capacity to the transmission system making it better able to address present and future needs.  A significant improvement in system performance with the proposed line in service is demonstrated by a 23.3 MW and 251.3 MVAR reduction in system losses and 86.2 MVAR increase in line charging that results at 2011 summer peak conditions.

Study Assumptions

The following assumptions were made in conducting this study:

- The 2011 Summer Peak case (created 12/06) would be the base case used for the load flow study.

- The only changes made to the generation dispatch in this case are as noted in the following bullets.   All generation in the study area was at or near its maximum in the base case.

- The Oak Grove net generation would be increased to 1710 MW (+ 130 MW) reflecting the signed SGIA.

- The Sandy Creek generation was added to the case at 925 MW per the signed SGIA.   It was assumed, even though the commercial operation date is September 2011, that the unit would be fully operational throughout most of the 2011 summer.

- The case generation-load balance following the generation additions (1055 MW) would be maintained by removing mothballed units that had been turned on to meet load in the case (905 MW) and by removing the smallest gas-fired steam units in ERCOT(150 MW).   This resulted in half of the balancing generation reduction being made in North Texas, and half being made in South Texas.

- The preceding changes would produce a reasonably likely transfer level for the information currently known.

- All valid single contingencies, single circuit and double circuit, would be run to test the sytem for this likely transfer level.

- Need For Project

Studies of 2011 summer peak conditions show that because of the heavy north to south transfer and the existence of only one 345 kV double circuit line in the west transfer corridor between Waco and Temple, loss of this double circuit 345 kV line or a portion of it results in a number of overloads.  Additionally, 345 kV outages in the east transfer corridor (Jewett to Houston) can shift additional power to and cause overloads on the west transfer corridor.

Four different 345 kV elements overload for 345 kV outages in the east and west transfer corridors.   These elements, their key contingencies and their associated overloads for the transfer level studied are as follows:

- Tradinghouse – Temple Pecan Creek Switch 345 kV circuit

  - Loss of Lake Creek – Temple Switch 345 kV circuit (111% of 956 MVA)

- Lake Creek – Temple Switch 345 kV circuit

  - Loss of Tradinghouse – Temple Pecan Creek (118% of 956 MVA)

  - Loss of TH Wharton – Jewett South & Obrien – Gibbons Creek (102% of 956 MVA)

  - Loss of Jewett North – Tomball & Jewett South – TH Wharton (104% of 956 MVA)

  - Loss of Tradinghouse – Lake Creek & Tradinghouse – Temple Pecan Creek (117% of 956 MVA)

- Gibbons Creek – Obrien 345 kV circuit

  - Loss of Tomball – Jewett North & King – Roans Prairie (108% of 1450 MVA)

- Temple Pecan Creek 345/138 kV autotransformer (114% of 680 MVA)

  - Loss of Temple Switch – Lake Creek & Temple Switch – Temple Pecan Creek (106 % of 680 MVA)

In addition there are 7 elements on the 138 and 69 kV systems that will overload as a result of 345 kV outages in the west transfer corridor between Waco and Temple at the studied transfer level.   These elements, their key contingencies, and their associated overloads are as follows:

- West Waco – Waco Woodway 138 kV circuit

  - Loss of Tradinghouse – Temple Pecan Creek & Lake Creek – Temple Switch 345 kV double circuit line (122 % of 214 MVA)

- Waco Woodway – Waco Woodway Tap 138 kV circuit

  - Loss of Tradinghouse – Temple Pecan Creek & Lake Creek – Temple Switch 345 kV double circuit line (104 % of 214 MVA)

- Waco Atco – Waco Woodway Tap 138 kV circuit

  - Loss of Tradinghouse – Temple Pecan Creek & Lake Creek – Temple Switch 345 kV double circuit line (104 % of 214 MVA)

- West Waco 138/69 kV autotransformer

  - Loss of Tradinghouse – Temple Pecan Creek & Lake Creek – Temple Switch 345 kV double circuit line (106 % of 76 MVA)

- Eddy – Troy 69 kV circuit

  - Loss of Tradinghouse – Temple Pecan Creek & Lake Creek – Temple Switch 345 kV double circuit line (108 % of 36 MVA)

- Lake Creek – Temple Pecan Creek 138 kV circuit (124% of 326 MVA)

  - Loss of Tradinghouse – Temple Pecan Creek & Lake Creek – Temple Switch 345 kV double circuit line (114 % of 326 MVA)

- Temple Pecan Creek – Temple Switch 138 kV line (141% of 326 MVA)

  - Loss of Temple Switch – Temple Pecan Creek & Lake Creek – Temple Switch 345 kV double circuit line (128% of 326 MVA)

The Excel spreadsheet included below shows the above results and the impact of adding the proposed line.   (Double click on the icon to open.)

It can be seen from the above spreadsheet results that the addition of the proposed line will eliminate all of the above overloads for the transfer level studied.    Also from the above spreadsheet it can be seen that the proposed line results in some new overloads.   The addition of this line will result in the need to upgrade the terminal equipment at TNP One on the Twin Oak – TNP One 345 kV double-circuit line.   Replacement of the limiting equipment necessary to obtain a 2000 ampere rating on each circuit will suffice..   It will also result in the need to upgrade the Temple Switch – Salado 345 kV circuit and the Temple Switch – Boggy Creek 138 kV line.   It is proposed that the 345 kV circuit be reconductored with 2-959.6 ACSS/TW to obtain 3200 amps of capacity, and that the 138 kV line be upgraded to operate the existing conductor at elevated temperature to obtain 1146 amps of capacity.   The Temple Switch – Salado 345 kV circuit does not overload at the transfer level used in this revised report (loads to 96%), but did overload at a slightly higher transfer level used in the initial study.   It was decided to include it here to provide additional transfer margin.   The results of a short circuit study modeling the proposed line did not identify any improvements needed that are not already planned.   See the Appendix attachment labeled ‘Short Circuit Study Results’.

The estimated total cost of the Bell County East to TNP One 345 kV double-circuit line, the construction of the Bell County East Switching Station, and the addition of three 345 kV circuit breakers at TNP One is approximately $69,337,000.  This cost includes the cost of the upgrades that are needed when this addition is made.   The basis for this cost estimate is shown in the Appendix attachment labeled ‘Costs Associated With Each Alternative’.

- Alternatives

Rebuild the Lake Creek – Temple Sw Sta 345 kV line, associated 138 and 69 kV lines listed above, and replace the West Waco 138/69 kV autotransformer.  This option would cost $80,039,000.  See Appendix attachment for details.  This option was more costly than the preferred option.   In addition, rebuilding 138 kV and 69 kV lines will not address the need for additional bulk transfer capacity, and continues a reliance on the load serving system to back up the bulk transmission system.   Generally, improvements on the load serving system provide a smaller increment of transfer capacity improvement than improvements on the bulk transmission system, and leave the transmission system less able to meet future needs.   Also, this option does not provide a significant improvement in system performance as the proposed project does, as is evidenced by the negligible reduction in system MW and MVAR losses from the base case (less than 10% of the loss reduction the proposed project provides).   For the preceding reasons this option was not chosen.

A second alternative would be to construct the Sandow – TNP One 345 kV double-circuit line.  This alternative would cost $74,418,000.  See Appendix attachment for details.  This option was more costly than the preferred option.  Also, the Sandow 345 kV Sw Sta would need to be rebuilt for a breaker and half arrangement requiring extensive clearances resulting in significant congestion.  Finally, unlike the proposed option, the advantages of tapping the new line into the Temple Sw Sta - Sandow 345 kV line -- reducing this line exposure and directing the power flow from these new generators more directly to the Temple – Killeen area where a large load is concentrated -- would not be gained with this alternative.   For the preceding reasons this option was not chosen.

Summary

The overloads seen in this study result from the fact that there is only a single 345 kV path between Waco and Temple Switch.   In the 2011 time frame it appears that there will be sufficient new generation in the area to create a high transfer level from North to South through the Waco to Temple corridor.   As a result, outages of this corridor can cause significant overloads on the underlying 138 kV and 69 kV networks as evidenced in this study.   The proposed project will create another 345 kV path from Waco to Temple eliminating these overloads.  The overloads seen can also be mitigated by reducing the interzonal transfers.   Consequently, if there is sufficient generation available on both sides of the transfer constraint to allow a redispatch to eliminate the overloads entirely, an assessment of the cost of the redispatch vs. the cost of project would be appropriate to determine whether this is an economic project.   The analyses performed in this study do not consider redispatch, so the resulting recommendations are based upon reliability rather than economic considerations; however, ERCOT’s independent study should establish whether an economic justification exists.

- Recommendation

TXU Electric Delivery recommends the construction of the 40.0-mile Bell County East – TNP One 345 kV double-circuit line using bundled 1590 kcmil ACSR conductor to get an ampacity of 2730 Amperes per circuit and the construction of the Bell County East Switching Station.   In addition, as a part of this proposal it is recommended that the limiting terminal equipment on the TNP One – Twin Oak double circuit line be upgraded to obtain a minimum rating of 2000 Amperes per circuit,  and that the Temple Switch – Salado 345 kV line be reconductored with 2-959 ACSS/TW to obtain a rating of 3200 amperes, and that the Temple Switch – Boggy Creek 138 kV line be upgraded to operate at elevated temperature to obtain a rating of 1146 amperes.  These system improvements are a necessary step in improving the north to south transfer capabilities and will add valuable capacity margin to the transmission system.   Even though the Sandy Creek generation is not scheduled to go commercial until September of 2011, it is recommended that this construction be completed prior to the unit being placed in test, or as soon as practical thereafter.

APPENDIX

Area Map

Area One-Line

Costs Associated With Each Alternative

Short Circuit Study Results

Response To Study Comments Received