| PRR Number | 732 | PRR Title | Automatic Voltage Regulator (AVR) Status – Compliance with NERC Reliability Standards |
| --- | --- | --- | --- |
| Date Posted |  | July 9, 2007 |  |
| Protocol Section(s) Requiring Revision |  | 6.5.7.2, QSE Responsibilities |  |
| Requested Resolution |  | Urgent status for this Protocol Revision Request (PRR) is requested to avoid exposure to possible violations of NERC Standards. |  |
| Revision Description |  | This PRR adds a requirement for telemetry of Generation Resource AVR status to comply with NERC Reliability Standards. |  |
| Reason for Revision |  | NERC Reliability Standard VAR-001-1, Requirements R4, R6 and R6.1 require the Transmission Operator to know the status of all transmission Reactive Power resources, including the status of AVRs on generators. In addition, NERC Reliability Standard VAR-002-1, to become effective 8/2/07, requires the Generator Operator to “…operate each generator connected to the interconnected transmission system in the automatic voltage control mode (automatic voltage regulator in service and controlling voltage)…” |  |
| Overall Market Benefit |  | Compliance to NERC Reliability Standards |  |
| Overall Market Impact |  | Unknown. |  |
| Consumer Impact |  | Unknown. |  |
| Credit Implications (Yes or No, and summary of impact) |  | TBD. |  |
| Relevance to Nodal Market |  | Yes. Language changes will need to be made to Nodal Protocols. |  |
| Nodal Protocol Section(s) Requiring Revision |  | 3.15.3, QSE Responsibilities Related to Voltage Support |  |

| Sponsor |  |
| --- | --- |
| Name | John Dumas |
| E-mail Address | jdumas@ercot.com |
| Company | ERCOT |
| Company Address | 2705 West Lake Drive Taylor, Texas 76574 |
| Phone Number | 512-248-3195 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

| Assumptions | 1 |  |  |
| --- | --- | --- | --- |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost | 1 | Unknown. | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit | 1 | Compliance with NERC Reliability Standards | Unknown. |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

Proposed Protocol Language Revision

6.5.7.2	QSE Responsibilities

(1)	QSE Generation Resources required to provide VSS are expected to have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the Operating Guides.

(2)	Each QSE’s Generation Resource providing VSS is expected to be compliant with the Operating Guides for response to transient voltage disturbance.

(3)	Each Generation Resource providing VSS must meet technical requirements specified in Section 6.10, Ancillary Service Qualification, Testing and Performance Standards.

(4)	Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) set to regulate generator terminal voltage in the voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is going On- or Off- line.  Each QSE shall telemeter to ERCOT the AVR status of each Generation Resource providing VSS to ERCOT.  An “ON” status indicates the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode and an “OFF” status indicates that the AVR is off or in a manual mode.   If the QSE changes the mode, other than under ERCOT direction, then the QSE shall promptly inform ERCOT. Any QSE-controlled power system stabilizers will be kept in service unless specifically permitted to operate otherwise by ERCOT.  QSEs’ control centers will monitor the status of their regulators and stabilizers, and shall report abnormal status changes to ERCOT.

(5)	QSEs shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits.

(6)	The reactive capability required must be maintained at all times the plant is On-line.

(7)	QSE shall advise ERCOT Operations whenever their Generation Resources are not operating at a power factor level as specified in the Operating Guides.  Upon such notice, ERCOT Operations, in conjunction with the appropriate TSP, shall investigate the situation with the goal of restoring the reported unit’s operation to within the specified power factor range.  Actions that ERCOT may take include the addition or removal of transmission reactive devices to/from service or a request to another Generator Resource within electrical proximity for the production of leading or lagging VARS (as appropriate) so as to equitably share the need for voltage support among Generation Resources.  Requests arising within the context of this subsection may not result in the operation of a Generation Resource outside of the specified reactive operating range.  Accordingly, Generation Resources are expected to voluntarily comply with these requests.  Nothing in this subsection is meant to supersede ERCOT’s Dispatch authority