| NOGRR Number | 007 | NOGRR Title | Nodal Operating Guides - Section 7, Telemetry and Communication |
| --- | --- | --- | --- |
| Date |  | July 17, 2007 |  |
| Submitter’s Information |  |  |  |
| Name |  | Jack Thormahlen on behalf of the Operating Guide Revisions Task Force (OGRTF) |  |
| E-mail Address |  |  |  |
| Company |  |  |  |
| Phone Number |  |  |  |
| Cell Number |  |  |  |
| Market Segment |  |  |  |

| Overall Market Benefit |  |
| --- | --- |
| Overall Market Impact |  |
| Consumer Impact |  |

Comments

Revised Proposed Nodal Operating Guide Language

ERCOT Nodal Operating Guides

Section 7:  Telemetry and Communication

(Effective Upon Texas Nodal Market Implementation)

7	Telemetry and Communication	3

7.1  	Obligation	3

7.1.1	ERCOT Responsibilities	3

7.1.2	QSE and TSP Responsibilities	3

7.1.2.1	 TSP and QSE Supplied Communications	4

7.2	Communications	5

7.2.1	ERCOT WAN	5

7.2.1.1	 Maintenance and Restoration	6

7.2.2	ERCOT ICCP Interface	6

7.2.2.1     Quality Codes	7

7.2.2.1.1	ICCP Quality Codes from Market Participants to ERCOT	7

7.2.2.1.2	ICCP Quality Codes from ERCOT to Market Participants	9

7.2.2.2  	Metric of Availability	10

7.3	Telemetry	10

7.3.1	Data from ERCOT to QSE’s	11

7.3.2	Data from ERCOT to TSP	12

7.3.3	Data from QSEs and TSPs to ERCOT	12

7.3.3.1	 Weather Zone Data	13

7.3.4	TSP and QSE Telemetry Restoration	13

7.3.5	QSE and TSP Data Acquisition	13

7.3.6	General Telemetry Performance Criterion	14

7.3.6.1	Critically Important Telemetry Performance Criterion	14

7.4	Calibration and Testing of Telemetry	15

7.4.1	Responsibility	15

7.4.2	Test Equipment	15

7.4.3	Disputes	16

2

2

2

3

4

4

5

6

7

7

8

8

9

9

1

1

1

1

1

1

1

1

# 7	Telemetry and Communication

7.1  	Obligation

7.1.1	ERCOT Responsibilities

ERCOT supplies interface requirements, equipment, and installation for the entire ERCOT Wide-Area Network (WAN), including equipment at each Qualified Scheduling Entity (QSE) and Transmission Service Provider (TSP) control facility and back-up location, as well as ERCOT’s control centers.  ERCOT’s responsibilities include:

(a)	Supply and install fully configured and tested customer premises equipment including routers, Channel Service Units/Data Service Units (CSU/DSUs), Local Area Network (LAN) switch/hub and all support equipment for management purposes;

(b)	Order and provision of local loop, network access point and transport;

(c)	Design, configure, test, and install network monitoring and management service;

(d)	Provide 24-hour network monitoring and management;

(e)	Provide 24x7 maintenance, with 4-hour response, for all ERCOT equipment located at Market Participant site; and

(f)	ERCOT will maintain internal procedures to respond to all maintenance or performance issues within a specified timeframe; and

(g)	ERCOT will be the single point of contact for all network issues and will notify the reporting Market Participant and the ERCOT shift supervisor within 10 minutes of an issue being reported.  Two hour updates are required until the issue is resolved.

7.1.2	QSE and TSP Responsibilities

(1)	TSPs and QSEs whose facilities connect to the ERCOT WAN are required to sign an agreement with ERCOT governing installation, operation and maintenance.  Users of the ERCOT WAN shall provide signal connections, uninterruptible power, physical security systems compliant with the applicable Critical Infrastructure Protection (CIP) requirement of the North American Electric Reliability Corporation (NERC) Reliability Standards, and physical space for ERCOT-supplied WAN interface equipment at their control centers, as well as 24-hour access for ERCOT installation and maintenance personnel.

(2)	At these facilities, computer and communications equipment connected to ERCOT WAN interfaces is the complete responsibility of the QSE or TSP.   Facilities shall have uninterruptible power supplies (UPS) capable of independently supplying all equipment connected to the ERCOT WAN for at least 72 hours.

(3)	Any TSP or QSE facility, whether primary or back-up, involved in the transfer of the data sets identified in Section 8, Attachment J, ERCOT Data Sets, will be required to connect directly to the ERCOT WAN primary private network and Point-to-Point paths. If a TSP and QSE utilize the same Energy Management System (EMS) and server network at one location and do not have an equipped backup center, ERCOT will only connect to this one location for the transfer of data.  If a TSP and QSE share a centralized private branch exchange (PBX), separate off-premise exchange (OPX) circuits will be terminated for each participant.  The Hotline will not be allowed to connect through the PBX system and is required for each Market Participant.

(4)	A QSE or TSP not involved in the transfer of the data identified in Section 8, Attachment J, ERCOT Data Sets, is not required to, but, may request ERCOT to provide an optional connection to the ERCOT private network.  When such a request is met by ERCOT, the QSE or TSP must then provide the above stated communications resources.

7.1.2.1		TSP and QSE Supplied Communications

(1)	Each TSP and QSE must provide internal facilities and communications to collect and furnish data and voice signals to the ERCOT WAN.  For TSPs these include, but may not be limited to, voice communications, Inter-Control Center Communication Protocol (ICCP), and SCADA for substations and other Transmission Facilities.  For QSEs, these include, but may not be limited to, voice communications, ICCP, and Supervisory Control And Data Acquisition (SCADA) for Resources and Loads.

(2)	QSEs and TSPs shall supply, implement, and maintain all data and voice communication facilities required to fulfill the obligations set forth in these Operating Guides.

(3)	Proper performance, maintenance and testing of communication paths not directly connected to the ERCOT WAN shall be the responsibility of the TSP or QSE providing the path.

(4)	QSEs communicating with Resources and TSPs communicating with substations are encouraged to use privately owned communication facilities.  Backup facilities utilizing common carriers, different privately owned facilities, or communications paths to a site are encouraged to provide increased reliability, i.e. separate paths to a site using different carrier, having multiple microwave paths leaving a site, etc.

7.2	Communications

The following sections describe the communications standards of the ERCOT Wide Area Network (WAN) utilized for Inter-Control Area Communications Protocol (ICCP) communications (Operational) and voice communications (Operational) that shall be used to exchange security and reliability information between:

(a)	ERCOT and a Qualified Scheduling Entity (QSE); and

(b)	ERCOT and a Transmission Service Provider (TSP).

7.2.1	ERCOT WAN

ERCOT shall provide for a WAN for secure communications path between ERCOT and the Market Participants in order to facilitate wholesale operations and frequency control as a single control area.  This communications network uses redundant, digital communications between ERCOT control centers and one or more facilities at each QSE and TSP.  As required by documents posted on the ERCOT MIS Secure Area, the ERCOT WAN shall have sufficient bandwidth capacity and speed to enable:

(1)	Real-time (telemetry) data exchange for frequency control and transmission security;

(2)	Operational voice communications for both normal and emergency use.  The ERCOT WAN supports both off-premise exchanges (OPX) with ERCOT’s control facilities and the ERCOT Hotlines; and

(3)	Data exchange to support applications programming interface (API) routines.  These include power scheduling, operating plans, outage requests, dispatch instructions, posting of information and other applications as determined by ERCOT.

7.2.1.1		Maintenance and Restoration

(1)	It is the joint responsibility of ERCOT WAN-connected Market Participants and ERCOT to coordinate maintenance and restoration activities so its reliability is not compromised.

(2)	All primary and back-up circuits shall be tested annually or as otherwise requested by ERCOT for end-to-end performance.

(3)	ERCOT will specify test procedures for Hotline and any back-up or alternate path voice circuits.

(4)	Test equipment to be used for the calibration or repair of communication equipment shall be certified to values of accuracy and precision.  The standard used for testing shall be superior to the tested equipment calibration requirements.

7.2.2	ERCOT ICCP Interface

The ICCP over the ERCOT WAN provides the Real-Time telemetry data from Market Participant computers, computer networks, or other devices.  Market Participants providing the data using an ICCP link must format their data and coordinate installation according to the ERCOT WAN Agreement found in the ERCOT Procedures.  The telemetry data furnished by a Market Participant’s ICCP link shall reflect the data quality codes of the individual data points as coordinated with ERCOT found in the Market Participant’s control computers and data collection system.  Market Participants shall provide documentation to ERCOT upon ERCOT’s request describing their control system quality codes and the mapping of their quality codes into the ERCOT defined quality codes.

7.2.2.1     Quality Codes

(1)	Status and analog telemetry data provided to ERCOT shall have the following associated quality codes:

(a)	“Valid” – represents analog or status data that the Market Participant and ERCOT considers valid;

(b)	“Suspect” - Any of the following: old value, old due to telemetry failure, considered suspect by the data owner, or otherwise should not be considered by ERCOT to be current.

(c)	“NOTVALID” – Value is invalid due to data acquisition/conversion errors or the initial value has never been established.

(d)	“Held” – Point has been taken off scan by Market Participant or otherwise removed from service.

(2)	Status and analog telemetry data provided to ERCOT shall have the following associated attributes:

(a)	“TELEMETERED” – Value was acquired from a field device.

(b)	“CALCULATED ” – Value is currently a calculated value and not estimated by a Market Participant State Estimator.

(c)	“MANUAL ” – represents analog or status data that is manually entered in the control system (not received from the field electronically).

(d)	“ESTIMATED” – Value was entered by a Market Participant’s State Estimator as an estimated value.

7.2.2.1.1	ICCP Quality Codes from Market Participants to ERCOT

The following Table 1: ICCP Quality Codes from Market Participants to ERCOT, describes the ICCP quality codes to be provided to ERCOT by the Market Participant.  The table includes:

(1)	The ICCP standard attribute name;

(2)	The ICCP standard named quality code of each attribute;

(3)	The conditions under which each ICCP quality code is to be set; and

(4)	A generic identifier of typical Real-Time database quality codes that would be mapped to the ICCP standard codes.

Table 1: ICCP Quality Codes from Market Participants to ERCOT

| ICCP Quality Attribute | ICCP Quality Code from Market Participant | Meaning | Generic RTDB Quality Code |
| --- | --- | --- | --- |
| Validity | VALID | Value is valid and can be trusted by ERCOT. | GOOD |
|  | HELD | Point has been taken off scan by Market Participant or otherwise removed from service. | NOT_IN_SERVICE |
|  | SUSPECT | Any of the following: old value, old due to telemetry failure, considered suspect by the data owner, or otherwise should not be considered by ERCOT to be current. | OLD (Stale) |
|  | NOTVALID | Value is invalid due to data acquisition/conversion errors or the initial value has never been established | BAD |
| Current Source | TELEMETERED | Value was acquired from a field device | REMOTE SOURCE |
|  | CALCULATED | Value is currently a calculated value and not estimated by a Market Participant State Estimator. | CALCULATED |
|  | MANUAL | Value was entered by a Market Participant operator. | MANUAL_ENTERED |
|  | ESTIMATED | Value was entered by a Market Participant’s State Estimator as an estimated value. | ESTIMATOR_ENTERED |
| Normal Value | NORMAL | The value is considered to be normal | (No special flag) |
|  | ABNORMAL | The value is considered to be abnormal | OFF_NORMAL |

7.2.2.1.2	ICCP Quality Codes from ERCOT to Market Participants

The following Table 2: ICCP Quality Codes from ERCOT to Market Participants, describes the ICCP quality codes to be provided to the Market Participant by the ERCOT, the conditions under which each ICCP quality code is set, and the translation from the local ERCOT Real-Time database quality codes to the related ICCP quality code.

Table 2:  ICCP Quality Codes from ERCOT to Market Participants

| ERCOT Local Quality Code | Meaning | ICCP Quality Code Sent to Market Participant | ICCP Quality Code |
| --- | --- | --- | --- |
| GOOD | Value is valid and can be trusted by Market Participant. | VALID | Quality |
| NOT_IN_SERVICE | Point has been taken off scan by ERCOT. | HELD |  |
| OLD (Stale) | Any of the following: old value, old due to telemetry failure, considered suspect by the original data owner, or otherwise should not be considered by Market Participant to be current. | SUSPECT |  |
| BAD OR UNINIT | Value is invalid due to data acquisition/conversion errors or the initial value has never been established | NOTVALID |  |
| NREMOTE | Value was acquired from a field device by the data owner. ERCOT is passing this information on to the Market Participant. | TELEMETERED | Current Source |
| NCALC AND NOT REPLACED | Value is currently a calculated value by ERCOT and not estimated by SE. | CALCULATED |  |
| MANREP | Value was manually entered either by the ERCOT operator or by the data owner | MANUAL |  |
| ESTREP | Value was entered by the ERCOT State Estimator as an estimated value. | ESTIMATED |  |
| NOT ABNORMAL | The value is considered to be normal by ERCOT per ERCOT’s database configuration | NORMAL | Normal Value |
| ABNORMAL | The value is considered to be abnormal by ERCOT per ERCOT’s database configuration | ABNORMAL |  |

7.2.2.2  	Metric of Availability

(1)	ICCP links must achieve a monthly availability of 98%, excluding approved Planned Outages.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data.  A link will be considered as available when at least 85% of the data defined on that link is successfully transferred to ERCOT with a “Valid” or “Held” and “Manual” quality code.  This will include establishing a process to coordinate downtime for ICCP links and database maintenance.

(2)	ICCP links shall use fully redundant data communication from the QSE and TSP control systems to the ERCOT System such that any single element of the communication system can fail and:

(a)	For server failures, complete Real-Time data transfer must be re-established within five minutes by automatic failover to alternate server(s); and

(b)	For all communication failures, complete Real-Time data transfer must continue to flow from the QSE and TSP control systems to the ERCOT System with updates of all data continuing at a 30 second or less scan rate.

7.3	Telemetry

(1)	Qualified Scheduling Entity (QSE) control centers required to supply Real-Time telemetry data to ERCOT shall use an Inter-Control Area Communications Protocol (ICCP) interface through the ERCOT Wide-Area Network (WAN).  QSEs shall also receive signals from ERCOT over the ICCP interface to implement frequency control.

(2)	Transmission Service Provider (TSP) control centers required to supply Real-Time telemetry data to ERCOT shall use an ICCP interface through the ERCOT WAN.

(3)	Each QSE and/or TSP shall continuously provide to ERCOT the telemetry data quantities that they are responsible for.  The frequency of update, means of communication to ERCOT, and format for each point provided by each Entity shall follow the specifications in Section 8, Attachment J, ERCOT Data Sets for that Entity, unless otherwise specified by ERCOT.  At the frequency specified in the Section 8, Attachment J, each update cycle shall provide new readings of all data points being monitored, not averages linked to prior cycle readings or repetition of readings from a previous cycle.  Design accuracy and availability of data points delivered to ERCOT shall satisfy the requirements and standards for telemetry performance and State Estimator performance as specified under Section 7.3.3, Data from QSEs and TSPs to ERCOT.

(4)	QSEs, Resources and TSPs are required to provide power operation data to ERCOT including, but not limited to:

(a)	Real-Time Resource data from QSEs;

(b)	Planned Outage information from Resources;

(c)	Transmission system network data used by any TSP’s control center, including:

(i)	Breaker and switch status of all ERCOT Transmission Elements;

(ii)	Line flow MW and MVar;

(iii)	Breaker and switch status connected to all Resources;

(iv)	Transmission Facility Voltages;

(v)	Transformer MW, MVar and TAP;

(vi)	Load MW and MVar; and

(vii)	Other data as required in Section 8, Attachment J, ERCOT Data Sets.

(d)	Real-Time Resource and Load Resource telemetry  data from QSEs;

(e)	Real-Time Generation Resource meter splitting telemetry data from QSEs;

(f)	Planned Transmission Outage information from TSPs;

(g)	Transmission system network model data including constraints from TSPs;

(h)	Current Operating Plans from QSEs; and

(i)	Dynamic Schedules from QSEs.

(5)	Real-Time telemetry data provided to ERCOT shall be at the same scan rate that the TSP or QSE control computers and data collection system obtains the data from telemetry.

7.3.1	Data from ERCOT to QSE’s

ERCOT shall provide all required data to QSE’s in accordance with these Operating Guides and the Protocols.  Section 8, Attachment J, ERCOT Data Sets provides the informational data sets that ERCOT will send to the QSEs.

7.3.2	Data from ERCOT to TSP

(1)	ERCOT shall provide operational data and issue instructions to the TSP in accordance with these Operating Guides and the Protocols.

(2)	ERCOT is required to provide the following power operation data to TSPs for the purpose of providing reliability information as determined by ERCOT:

(a)	Status of any breakers and switches in ERCOT's Real-Time data base;

(b)	State Estimator solutions;

(c)	Transmission line flows and voltages;

(d)	Transformer information;

(e)	QSE Resource data; and

(f)	Voltage schedules at transmission busses.

(3)	ERCOT will give notice to the Entities supplying the above list of data to ERCOT upon the initial provision of such data to the TSP.

7.3.3	Data from QSEs and TSPs to ERCOT

(1)	QSEs and TSPs shall provide Real-Time monitoring of power system quantities to ERCOT as defined in the Operating Guides and Protocols.  Section 8, Attachment J, ERCOT Data Sets, of this Operating Guide specifies the format and description for the content of each type of data point that ERCOT may request from TSPs and QSEs.  Not all data points in Section 8, Attachment J, ERCOT Data Sets are required from each Entity.  ERCOT shall work with TSPs and QSEs to determine the required data using the methodology presented in the Protocols.   At a minimum, all the device status and analog measurements that the TSPs and QSEs use to operate their facilities and facilities for which they are a Designated Agent shall be provided.    Ultimately, it is the responsibility of the TSPs and QSEs to provide all data requested by ERCOT as set forth in the Protocols and Operating Guides.

(2)	Real-Time telemetry data from QSEs used to supply power or Ancillary Services shall be integrated by ERCOT and checked against settlement meter values on a monthly basis.

(3)	Where multiple generators share a single net settlement meter, the ratio of integrated Real-Time data from each generator shall be used to proportion the total settlement quantity.

(4) 	Each QSE and TSP shall notify ERCOT as soon as practicable when telemetry will not be available or is unreliable for operational purposes. When ERCOT receives notification, these points shall be removed from performance metrics calculations.

(5)	Each QSE and TSP shall notify ERCOT as soon as practicable when telemetry is returned to normal state.

7.3.3.1		Weather Zone Data

(1)	A TSP that is responsible for providing Weather Zone tie-line measurement data to ERCOT is required to establish a backup to the primary source.

(2)	TSPs having an Energy Management System (EMS) with a native ICCP application capable of four second periodic data set transfers with minimum 300 points per data set, and hot standby backup ICCP servers with automatic fail-over capability, shall provide an additional ICCP association across the ERCOT WAN for the transfer of Weather Zone tie line measurements.  ICCP nodes should exist at primary and backup facilities.

7.3.4	TSP and QSE Telemetry Restoration

(1)	Real-Time telemetry data shall be provided continuously.  Data that is inaccurate or of bad quality, whether failed or in error, must be restored promptly by the provider of the telemetry data.  It is recognized that some data may be of more importance than other data.  ERCOT will inform the TSP or QSE of data in this category that needs to be repaired to service as quickly as possible.  QSEs and TSPs shall provide information to ERCOT of any and all corrective actions taken to restore reported telemetry errors to ERCOT upon request.  When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, take corrective action to either:

(a)	Calibrate/repair the mis-behaving equipment;

(b)	Request an Outage to schedule calibration/repair of the mis-behaving equipment;

(c)	Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame; or

(d) 	Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.

(2)	Before ERCOT requests review/re-calibration of a telemetry problem with a piece of equipment it shall discuss the problem with the provider to attempt to arrive at a consensus decision for the most appropriate action.

7.3.5	QSE and TSP Data Acquisition

Suppliers of Real-Time telemetry data must collect and process telemetry data from field equipment at their control centers before passing to the ERCOT interface.  The equipment and processes are owned and operated entirely by the supplier.  Traditionally, utilities have used both analog and digital methods of transmission at existing facilities.  It is the responsibility of the QSEs and TSPs who supply other Entities’ data to ERCOT to also arrange for reliable delivery of telemetry data from the field equipment from the other entities in order to support the requirements in these Operating Guides.

7.3.6	General Telemetry Performance Criterion

The following criteria will apply to Real-Time telemetry provided to ERCOT:

(1)	The TSP shall maintain the sum of flows into any telemetered substation less than the greater of 5 MW or 5% of the largest line Normal Rating at each telemetered substation.

(2)	Each QSE or TSP shall provide telemetry data to ERCOT such 98% of all telemetry provided to ERCOT achieves a quarterly availability of at least 80% percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with good quality codes at the scheduled periodicity.

(3)	Exceptions to the general telemetry performance criterion shall be made for data points that do not have a market impact in the quality of the State Estimator solution or required for the reliable operation of the ERCOT Transmission Facilities.  Some examples of these are:

(a)	Substation with no more than two transmission lines and less than 10 MW of load;

(b)	Connection of Loads along a continuous, non-branching circuit that may be combined for telemetry purposes; and

(c)	Substations connected radially to the bulk transmission system.

7.3.6.1	Critically Important Telemetry Performance Criterion

(1)	ERCOT shall create a list of those MW/MVar telemetry pairs, not exceeding 10% of the Transmission Elements in ERCOT, and up to 20 voltage points that are identified as critically important to reliability, system observability, support of State Estimator performance, or are of a commercial Market concern. This list of critically important telemetry must meet more stringent criteria for accuracy and availability where specifically addressed. ERCOT shall review and publish this list annually. ERCOT shall use the following criteria to identify critically important telemetry:

(a)	Loss of telemetry points that result in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(b)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(c)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on transmission facilities designated as critically important to transmission reliability by ERCOT. A list of these critical facilities will be published annually.

(d)	Telemetry necessary to monitor Transmission Elements identified as causing 80% of congestion cost in the year for which the most recent data is available.

(e)	Telemetry necessary to monitor the 20 most voltage critical buses designated by ERCOT and approved by the Technical Advisory Committee (TAC) each October.

(2)	Each QSE or TSP shall provide identified critical telemetry data to ERCOT such that 95% percent of the critically important telemetry identified by ERCOT must achieve a quarterly availability of at least 90% percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with “Valid” or “Held” and “Entered” quality codes at the scheduled periodicity.

7.4	Calibration and Testing of Telemetry

7.4.1	Responsibility

It is the responsibility of the owner of telemetry equipment to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds that which is specified in the ERCOT Protocols and these Operating Guides, for both the overall system and for individual equipment.  Coordination of calibration and testing activities with ERCOT is also the responsibility of the owner.  Upon ERCOT’s request, each Transmission Service Provider (TSP) and Qualified Scheduling Entity (QSE) shall provide ERCOT access to its preventive maintenance and calibration test procedures and records for purposes of ensuring accurate telemetry of data.   If a TSP and/or QSE repeatedly fails other telemetry metrics defined in these Operating Guides, ERCOT may require the owner to revise its procedures to ensure accuracy and availability of telemetry data.

7.4.2	Test Equipment

Test equipment and to be used for the calibration or repair of telemetry and associated equipment shall be certified to values of accuracy and precision. The standard used for testing shall be superior to the tested equipment calibration requirements.

7.4.3	Disputes

Where a dispute over the accuracy or performance of any telemetry equipment exists, ERCOT may request a comparison of accuracy and/or a joint calibration of affected equipment.