| NOGRR Number | 005 | NOGRR Title | Nodal Operating Guides – Section 5, Planning |
| --- | --- | --- | --- |
| Date |  | July 17, 2007 |  |
| Submitter’s Information |  |  |  |
| Name |  | Rick Keetch on behalf of the Operating Guide Revisions Task Force (OGRTF) |  |
| E-mail Address |  | rkeetch@ercot.com |  |
| Company |  | Reliant Energy |  |
| Phone Number |  | 713-497-2526 |  |
| Cell Number |  |  |  |
| Market Segment |  | Power Marketer |  |

| Overall Market Benefit |  |
| --- | --- |
| Overall Market Impact |  |
| Consumer Impact |  |

Comments

The OGRTF proposes that the Operations Working Group (OWG) recommend approval of NOGRR005 as follows.  This incorporates CenterPoint Energy and LCRA comments and modifications by the OGRTF.

Revised Proposed Nodal Operating Guide Language

ERCOT Nodal Operating Guides

Section 5:  Planning

(Effective Upon Texas Nodal Market Implementation)

5	Planning	1

5.1	Planning Criteria	1

5.1.1	Introduction	1

5.1.2	Real-Time and Short Term Planning	2

5.1.3	Load Forecasts	2

5.2	Resource Capability	2

5.3	Transmission Reliability Studies	2

5.4	Reports of Studies	4

5.5	System Modeling Information	4

5.5.1	System Assessments	6

5.5.2	ERCOT Clarifications and Definitions of NERC Reliability Standards Contingency Categories C and D	8

# 5	Planning

5.1	Planning Criteria

5.1.1	Introduction

(1)	The ERCOT System consists of those generation and Transmission Facilities (60 kV and higher voltages) that are controlled by individual Market Participants (MPs) and that function as part of an integrated and coordinated power supply network.  Each reference in this document to MPs includes Generation Resources. Qualified Scheduling Entities (QSEs), Competitive Retailers (CRs), Transmission Service Providers (TSPs), Distribution Service Providers (DSPs) and others that use the ERCOT Transmission Grid.

(2)	To maintain reliable operation of the ERCOT System, it is necessary that all MPs observe and subscribe to certain minimum planning criteria. The criteria set forth herein, combined with the applicable North American Electric Reliability Corporation (NERC) Reliability Standards constitute the aforementioned minimum planning criteria. Tests outlined herein shall be performed to determine conformance to these minimum criteria; however, ERCOT recognizes that events more severe than those outlined in these criteria could cause grid separation, other tests may also be performed, if necessary, for information purposes.

(3)	The complexity and uncertainty inherent in the planning and operation of the ERCOT System make exhaustive studies impracticable; therefore, to gain maximum benefit from the limited number of tests performed, the selection of the specific tests and the frequency of their performance will be made solely upon the basis of the expected value of the reliability information obtainable from the test.

(4)	It is the responsibility of each Transmission Service Provider (TSP) to perform tests appropriate to ensure the reliability of its Transmission Facilities.  Further the TSP may recommend additional studies by ERCOT or the Reliability Operations Subcommittee (ROS).  Additional tests which may affect multiple TSPs or the ERCOT System as a whole may be studied.  Upon consideration of such recommendations, ERCOT and the ROS shall coordinate the performance of such studies, as necessary, to assess the reliability of the planned ERCOT System.

(5)	ERCOT Regional Planning Groups or ERCOT System Planning shall determine and demonstrate the need for any static and/or dynamic Reactive Power capability in excess of the explicit requirements of the ERCOT Protocols and Operating Guides that is necessary to ensure compliance with the ERCOT Planning Criteria. ERCOT Transmission Planning shall establish specific TSP responsibility for any associated facility additions.

(6)	ERCOT, in cooperation with the TRE, will review the ERCOT Planning Criteria every three years to ensure it meets the requirements in the NERC Reliability Standards.  ERCOT, in cooperation with the TRE, will periodically review the planning criteria, procedures, and practices of individual ERCOT TSPs to ensure consistency with all applicable NERC Reliability Standards and the ERCOT Planning Criteria.

5.1.2	Real-Time and Short Term Planning

ERCOT will conduct Real-Time and short term planning based on the security criteria established in the ERCOT Protocols and these Operating Guides.  Operations during Forced and Planned Outages will also follow these criteria. Line ratings are provided to ERCOT in accordance with ERCOT Protocols and these Operating Guides.     ERCOT will employ congestion management, Special Protection Systems (SPS), Remedial Action Plans (RAPs) and transmission switching schemes to facilitate the market use of the ERCOT Transmission Grid while maintaining system security and reliability in accordance with ERCOT and NERC Reliability Standards.  ERCOT will address operating conditions under which the reliability of the ERCOT System is inadequate and no solution is readily apparent in accordance with the ERCOT Protocols and these Operating Guides.

5.1.3	Load Forecasts

(1)	Each DSP or its Designated Agent directly interconnected with the ERCOT Transmission Grid shall provide annual Load forecasts to ERCOT as outlined in the ERCOT Annual Load Data Request (ALDR) Procedures.

(2)	For each substation not owned by either a TSP or a DSP, the owner shall provide a substation Load forecast to the directly-connected TSP sufficient to allow it to adequately include that substation in its ALDR response.

(3)  	If load data is not timely submitted on the schedule and in the format defined by the TSP, then ERCOT shall calculate loads based on historical data and insert these loads into the load flow cases during DataSet A and DataSet B annual updates.

5.2	Resource Capability

(1)	ERCOT will periodically determine the minimum reserve margin required to ensure the adequacy of installed generation and other resource capability in ERCOT.  ERCOT or the Public Utility Commission of Texas (PUCT) may also approve specific Market Participant (MP) requirements to ensure that the required minimum reserve margin is maintained.

(2)	ERCOT maintains a database containing existing and proposed generation or other resource capability historical and projected values for demand and energy and proposed major transmission grid additions. This database is updated periodically and the Capacity Demand Reserve (CDR) Working Paper is produced annually by ERCOT.

5.3	Transmission Reliability Studies

(1)	The interconnection philosophy of ERCOT is to minimize loss of Load by remaining interconnected.  Interconnected system planning will include steady state and dynamic simulated testing by ERCOT and Transmission Service Providers (TSPs) to represent specific occurrences for each type of contingency specified below or listed in Table 5-1, Transmission Systems Standards — Normal and Contingency Conditions, in Section 5.5.1, System Assessments, and the NERC Reliability Standards.  The term “generating unit”, as used in Table 5-1, for the purpose of reliability studies shall be defined as the largest single generating unit operating at a given voltage level at each plant location.  In the case of a Combined Cycle Facility, the term “generating unit”, as used in Table 5-1, shall be considered as the total generating capacity of the entire train as defined in Section 1, Overview.  Also included in Table 5-1 are “ERCOT Clarifications and Definitions” that are applicable to studies for NERC Reliability Standards Categories C and D.

(2)	The contingency studies will be performed for reasonable variations of Load level, generation schedules, planned transmission line Maintenance Outages, and anticipated power transfers.  At a minimum, this should include projected Loads for the upcoming summer and winter seasons and a five-year planning horizon.  The TSPs involved should plan to resolve any unacceptable study results through the provision of Transmission Facilities, the temporary alteration of operating procedures (i.e., RAPs), temporary Special Protection Systems (SPSs), or other means as appropriate.

(3)	While the requirements listed in Table 5-1 address most ERCOT planning concerns, studies will also be conducted to ensure that Credible Single Contingencies do not result in the following:

(a)	Cascading or uncontrolled outages;

(b)	 Instability of generating units at multiple plant locations; or

(c)	Interruption of service to firm demand or generation other than that isolated by the double-circuit loss, following the execution of all automatic operating actions such as relaying and special protection systems.  Furthermore, the loss should result in no damage to or failure of equipment and, following the execution of specific non-automatic predefined operator-directed actions (i.e., RAPs), such as generation schedule changes or curtailment of interruptible Load, should not result in applicable voltage or thermal ratings being exceeded.

(4)	Voltage stability margin shall be sufficient to maintain post-transient voltage stability   under the following study conditions:

(a)	For each ERCOT defined area, a 5% increase in Load above expected peak supplied from resources external to the ERCOT defined area; and NERC Category A or B operating conditions (see Table 5-1 in Section 5.5.1, System Assessments );

(b)	For each ERCOT defined area, a 2.5% increase in Load above expected peak supplied from resources external to the ERCOT defined area; and NERC Category C operating conditions (see Table 5-1 in Section 5.5.1, System Assessments).

(5)	ERCOT is responsible for gathering Load data for use in the ERCOT Load flow cases via the ALDR.  The Reliability and Operations Subcommittee (ROS) coordinates with ERCOT in the performance of steady state and dynamic simulation studies of the bulk electric system to determine the impact on the planned system of occurrences of the types of contingencies listed in the NERC Reliability Standards.  The Steady State Working Group (SSWG), Dynamics Working Group (DWG) and System Protection Working Group (SPWG) shall coordinate with ERCOT to create databases and perform tests as outlined in these criteria.

(6)	These databases created by the ROS working groups are available for use by MPs. The individual TSPs affected by identified issues will pursue appropriate solutions.  It is the responsibility of the individual TSPs to use these databases to:

(a)	Perform steady state and dynamic tests appropriate to evaluate the compliance of their Transmission Facilities within the ERCOT Planning Criteria; and

(b)	Recommend other tests which examine effects of importance to multiple TSPs.

(7)	Other System Planning requirements and expectations are outlined in ERCOT’s System Planning Charter.

5.4	Reports of Studies

ERCOT annually directs the preparation of Department of Energy (DOE) reports.  These reports address the adequacy of the ERCOT System and provide input to various North American Electric Reliability Corporation (NERC) reports.  The adequacy of the planned ERCOT System is based on studies performed by ERCOT and individual Transmission Service Providers (TSPs).

5.5	System Modeling Information

Information on existing and future ERCOT System components and topology is necessary for ERCOT to create databases and perform tests as outlined in these criteria.  To ensure that such information is made available to ERCOT, the following actions by Market Participants (MPs) are required:

(1)	Each TSP, or its Designated Agent, shall provide accurate modeling information for all ERCOT Transmission Facilities owned or planned by the Transmission Service Provider (TSP).  The information provided shall include, but not be limited to, the following:

(a)	Information necessary to represent the TSP’s Transmission Facilities in any model of the ERCOT Transmission Grid whose creation has been approved by ERCOT, including modeling information detailed in procedures of the Steady State Working Group (SSWG), Dynamics Working Group (DWG), and System Protection Working Group (SPWG);

(b)	Identification of a designated contact person, generally regarded as the working group TSP representative, responsible for providing answers to questions ERCOT may have regarding the information provided; and

(c)	TSP owned or operated Transmission Facility data provided and used to accurately represent a Transmission Facility in a model shall be consistent to the extent practicable with data provided and used to represent that same Transmission Facility in any other model created to represent a time period during which the Transmission Facility is expected to be physically identical.   All existing transmission lines’ and transformers’ impedances, or equivalent branch circuit impedance, and ratings - Normal and Emergency - shall be identical, to the extent practicable.  If all normally closed breakers and switches are closed and normally open breakers and switches are open in the Network Operations Model, the calculated line flows between substations in the Annual Planning Model shall be consistent, when all models use the same load magnitude and distribution, generation commitment and dispatch, and voltage profile. ..

(2)	Any long-term changes to the reactive capability must be provided by the facility owner to ERCOT, as planned at least 30 days prior to implementation and as built no later than 30 days after implementation, as changes or upgrades are made during the life of the Reactive Power facilities.

(3)	Further, each TSP owning or planning Transmission Facilities or its Designated Agent shall attend the scheduled meetings and otherwise participate in the activities of the SSWG, DWG, and the SPWG, unless specifically exempted from these activities by ERCOT.

(4)	Each Generation Resource, or its Designated Agent, shall provide accurate modeling information for each existing or publicly-announced ERCOT generating unit for which it is the majority owner.  The information provided shall include, but not be limited to, the following:

(a)	Information necessary to represent the Generation Resource’s generation and interconnection facilities in any model of the ERCOT System whose creation has been approved by ERCOT, including modeling information detailed in procedures of the SSWG, DWG, and SPWG; and

(b)	Identification of a designated contact person, generally regarded as the TSP working group representative responsible for providing answers to questions ERCOT may have regarding the information provided.

(5)	Typical or representative information may be provided for planned facility additions or modifications, but such information shall be revised using actual design or construction information no later than 90  days after the facility has been energized or otherwise placed into service.

(6) 	Congestion Revenue Rights (CRR) Network Model Outage determination uses network topology of the CRR Network Model identified by ERCOT Staff.  This must include monthly Outages that demonstrate significant impact to the transfer capability.  The Outages included in the CRR Network Model shall be posted by ERCOT on the Market Information System (MIS) Secure Area.  These Outages shall be consistent with the model posting requirements and with accompanying cause and duration information, as indicated in the Outage Scheduler in Protocol Section 7.5.1, Nature and Timing.  The CRR Network Model criteria are:

(a)	Consecutive or continuous Outages greater than or equal to five days;

(b)	Transmission Elements included in the definition of a Hub;

(c)	Transmission Elements in a 345 kV Transmission Facility;

(d)	Direct Current (DC) interconnections;

(e)	Approved Outages that requires the use of a Block Load Transfer (BLT); and

(f)	Approved Outages that were proposed in the “Greater than 90 days” timeline in Protocol Section 3.1.5.3, Timelines for Response by ERCOT for TSP Requests.

5.5.1	System Assessments

ERCOT and TSPs or their Designated Agent shall conduct reliability assessments as required by the NERC Reliability Standards and Public Utility Commission of Texas (PUCT) Substantive Rules.  MPs shall supply all relevant data required to assist in the preparation of these assessments as requested by ERCOT.  This is in addition to data required by the ERCOT Protocols, ERCOT System Planning Charter or these Operating Guides.

| Table 5-1: Transmission Systems Standards — Normal and Contingency Conditions |  |  |  |  |
| --- | --- | --- | --- | --- |
| Category | Contingencies | System Limits or Impacts |  |  |
|  | Initiating Event(s) and Contingency Element(s) | System Stable and both Thermal and Voltage Limits within Applicable Ratingsa | Loss of Demand or Curtailed Firm Transfers | Cascading Outages |
| A: No Contingencies | All Facilities in Service | Yes | No | No |
| B: Event resulting in the loss of a single element. | Single Line Ground (SLG) or 3-Phase (3Ø) Fault, with Normal Clearing: 1. Generator 2. Transmission Circuit 3. Transformer Loss of an Element without a Fault. | Yes Yes Yes Yes | No b No b No b No b | No No No No |
|  | Single Pole Block, Normal Clearing e: 4. Single Pole (dc) Line | Yes | Nob | No |
| C: Event(s) resulting in the loss of two or more (multiple) elements. | SLG Fault, with Normal Clearing e: 1. Bus Section 2. Breaker (failure or internal fault) | Yes Yes | Planned/Controlledc Planned/Controlledc | No No |
|  | SLG or 3Ø Fault, with Normal Clearinge, Manual System Adjustments, followed by another SLG or 3Ø Fault, with Normal Clearinge: 3. Category B (B1, B2, B3, or B4) contingency, manual system adjustments, followed by another Category B (B1, B2, B3, or B4) contingency | Yes | Planned/Controlledc | No |
|  | Bipolar Block, with Normal Clearinge: 4. Bipolar (dc) Line Fault (non 3Ø), with Normal Clearinge: 5. Any two circuits of a multiple circuit towerlinef | Yes Yes | Planned/Controlledc Planned/Controlledc | No No |
|  | SLG Fault, with Delayed Clearinge (stuck breaker or protection system failure): 6. Generator 7. Transmission Circuit 8. Transformer 9. Bus Section | Yes Yes Yes Yes | Planned/Controlledc Planned/Controlledc Planned/Controlledc Planned/Controlledc | No No No No |
| D d: Extreme event resulting in two or more (multiple) elements removed or cascading out of service | 3Ø Fault, with Delayed Clearinge (stuck breaker or protection system failure): 1. Generator 2. Transmission Circuit 3. Transformer 4. Bus Section | Evaluate for risks and consequences. - May involve substantial loss of customer Demand and generation in a widespread area or areas. - Portions or all of the interconnected systems may or may not achieve a new, stable operating point. - Evaluation of these events may require joint studies with neighboring systems |  |  |
|  | 3Ø Fault, with Normal Clearinge: 5. Breaker (failure or internal fault) |  |  |  |
|  | 6. Loss of towerline with three or more circuits 7. All transmission lines on a common right-of way 8. Loss of a substation (one voltage level plus transformers) 9. Loss of a switching station (one voltage level plus transformers) 10. Loss of a all generating units at a station 11. Loss of a large load or major load center 12. Failure of a fully redundant Special Protection System (or remedial action scheme) to operate when required 13. Operation, partial operation, or misoperation of a fully redundant Special Protection System (or remedial action scheme) in response to an event or abnormal system condition for which it was not intended to operate 14. Impact of severe power swings or oscillations from disturbances in another Regional Reliability Organization. |  |  |  |

Footnotes to Table 5-1:

- (a)	Applicable rating refers to the applicable Normal and Emergency facility thermal Rating or system voltage limit as determined and consistently applied by the system or facility owner.  Applicable Ratings may include Emergency Ratings applicable for short durations as required to permit operating steps necessary to maintain system control.  All Ratings must be established consistent with applicable NERC Reliability Standards addressing Facility Ratings.

- (b)	Planned or controlled interruption of electric supply to radial customers or some local Network customers, connected to or supplied by the Faulted element or by the affected area, may occur in certain areas without impacting the overall reliability of the interconnected transmission systems. To prepare for the next contingency, system adjustments are permitted, including curtailments of contracted Firm (non-recallable reserved) electric power Transfers.

- (c)	Depending on system design and expected system impacts, the controlled interruption of electric supply to customers (load shedding), the planned removal from service of certain generators, or the curtailment of contracted Firm (non-recallable reserved) electric power Transfers may be necessary to maintain the overall reliability of the interconnected transmission systems.

- (d)	A number of extreme contingencies that are listed under Category D and judged to be critical by the transmission planning entity(ies) will be selected for evaluation. It is not expected that all possible facility outages under each listed contingency of Category D will be evaluated.

- (e)	Normal clearing is when the protection system operates as designed and the Fault is cleared in the time normally expected with proper functioning of the installed protection systems.  Delayed clearing of a Fault is due to failure of any protection system component such as a relay, circuit breaker, or current transformer, and not because of an intentional design delay.

- (f)	System assessments may exclude these events where multiple circuit towers are used over short distances (e.g., station entrance, river crossing) in accordance with Regional exemption criteria.

5.5.2	ERCOT Clarifications and Definitions of NERC Reliability Standards Contingency Categories C and D

5.5.2.1	Category C

(1)	Bus Section Definition - "Bus Section" shall be interpreted to mean any section of buswork, which would be isolated by normal relay/breaker operation when faulted.

(2)	Manual System Adjustments Definition - "Manual System Adjustments" shall be interpreted to include only operator actions that:

(a)	Would be made no later than one hour after clearing of the first fault;

(b) 	Are made using remote control capability or communications with other operators having such capability;

(c) 	Include circuit switching, changes in the schedules of generating units operating at clearing of the first fault, and changes in the schedules of other generating units that can contribute within one hour; and

(d) 	Exclude the physical repair or replacement of damaged equipment and the starting of any generating unit that cannot contribute within one hour.

(3)	Planned Loss of Demand or Curtailed Firm Transfer Definition - All Load interruption, generator tripping, or generation schedule changes must be either automatic or prearranged with associated written operating procedures.  Actions must be executable in time to avoid any equipment damage or safety violations, but in any case within 30 minutes of fault clearing.

(4)	Cascading Outage Definition - Cascading Outages are defined as the uncontrolled loss of any system facilities or load, whether because of thermal overload, voltage collapse, or loss of synchronism, except those occurring as a result of fault isolation.

(5)	Implementation Guidelines - Evaluation of all the possible combination of facility Outages under Category C is not required. Each TSP with bulk Transmission Facilities will evaluate one or more Category C contingencies annually.  The contingencies selected may be based on the results of related studies or actual events.  In either case, the selected contingencies must indicate more severe results or impacts based on the engineering judgment of the facility owner, ERCOT or any TSP.  An explanation of why any remaining contingencies would produce less severe system results shall be available as supporting information.

5.5.2.2	Category D

(1)	For the purpose of evaluating the consequences resulting from a Category D event, a Large Load or Major Load Center is an electrical demand of between 50 and 500 MW.  This may be a large single Load or a group of electrically close Loads. The loss of this demand will not include any other system elements other than those directly connected.

(2)	Evaluations of Category D contingencies are required to be performed annually.  Evaluations should be performed for the following:

(a)	Contingencies previously studied for which the conditions assumed in the study have changed significantly and which may adversely affect the results of the study; and

(b)	Contingencies not previously studied that, based on the results of related studies or actual events may in the engineering judgment of the facility owner, ERCOT or any TSP, have unacceptable consequences.