## Slide 1: Parkdale Dynamic Reactive Project Technical Advisory Committee Dan Woodfin

## Slide 2: Description of Project
600 Mvar of dynamic reactive capability
Parkdale Station identified as a suitable site
A portion of proposed capability in service by 2009 peak
Estimated cost range: $45 – 97.5 M
Additional consultant study required to determine the most appropriate technology

## Slide 3: Reliability Need for Project
Voltage Recovery:
  Ensure that post-contingency system voltages recover to acceptable levels.
Load Shedding:
  Do not rely on UVLS schemes to prevent voltage collapse for NERC Category C contingencies.
Load and Generation Forecast for DFW Area:
  High import into the DFW area requires dynamic reactive support. 2009 demand will exceed local generation by approximately 13,500 MW. New emissions restrictions will likely restrict the availability of generation resources within the DFW area.

## Slide 4: DFW Load and Generation

## Slide 5: Independent Review Results
DFW dynamic reactive capability is required
Amount dependent upon DFW generation availability
  100 Mvar when all generation resources available.
  500 Mvar when 4 non-SCR units unavailable.
  600 Mvar when an additional SCR unit unavailable.
Dynamic simulations utilized typical static condenser model
  Required amount of dynamic capability to achieve a similar system response may depend on the technology used.

## Slide 6: Independent Review Results
Investigated additional impacts
  Faster fault clearing times may improve system response but do not address the fundamental need for dynamic reactive support in the DFW area under high import scenarios.
  Slow voltage recovery and potential voltage collapse are exacerbated by peak load conditions and the unavailability of DFW generation resources.
  Improving DFW load power factor did not provide any voltage recovery benefit for simulated contingencies.

## Slide 7: ERCOT Support for the Project
Additional Recommendations
  Oncor should proceed with their planned consultant study to assist them in selecting the most appropriate technology for providing dynamic reactive capability.
  Oncor should consider the possibility of utilizing more than one location to deploy a total of 600 MVAr (or equivalent dynamic reactive capacity to provide the same response depending on the location and technology used).
The Stakeholder review period for this project was held in May 2007
There were no comments on this project
ERCOT Staff recommends that the project be endorsed by the Board