ERCOT Operations Report

July 2007 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration |  |
| --- | --- | --- | --- |
| 07/02 19:31:46 | 59.810 | 2 m 18 s | 2 unit trips totaling 943 MW. Laar deployment initiated at 19:37. |
| 07/02 19:43:06 | 60.132 | 8 m 56 s |  |
| 07/03 13:27:14 | 59.850 | 56 s | 580 MW unit trip |
| 07/16 09:59:42 | 59.863 | 43 s | 625 MW unit trip |
| 07/16 22:21:28 | 59.885 | 6 s | 3 unit train tripped totaling 425 MW. |
| 07/20 04:23:02 | 59.893 | 4 s | 2 unit train tripped totaling 315 MW. |
| 07/20 22:05:34 | 59.890 | 8 s | -650 MW ERCOT SCE during a 3050 MW schedule change |
| 07/24 15:17:10 | 59.862 | 16 s | 650 MW unit trip |
| 07/25 09:19:06 | 59.891 | 16 s | 350 MW unit trip |

Deployed Responsive (Reported Above)

| ID | Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- | --- |
| 1 | 7/2 19:31:54 | 7/2 19:46:06 | 14:12 | 849.70 |  |
| 2 | 7/3 13:27:16 | 7/3 13:40:22 | 13:06 | 610.57 |  |
| 3 | 7/13 23:59:08 | 7/14 0:10:54 | 11:46 | 417.22 | SCE |
| 4 | 7/16 9:59:44 | 7/16 10:09:18 | 09:34 | 544.43 |  |
| 5 | 7/16 22:21:32 | 7/16 22:27:38 | 06:06 | 432.49 |  |
| 6 | 7/17 16:10:38 | 7/17 16:17:34 | 06:56 | 330.73 | Unit Trip |
| 7 | 7/20 4:23:00 | 7/20 4:36:18 | 13:18 | 391.77 |  |
| 8 | 7/20 22:05:34 | 7/20 22:11:20 | 05:46 | 407.05 |  |
| 9 | 7/24 15:17:12 | 7/24 15:26:11 | 08:59 | 549.51 |  |
| 10 | 7/25 9:19:08 | 7/25 9:32:50 | 13:42 | 417.22 |  |
| 11 | 7/25 9:38:30 | 7/25 9:49:54 | 11:24 | 340.90 | Server/ Communication |
| 12 | 7/27 23:00:14 | 7/27 23:09:20 | 09:06 | 315.46 | SCE |
| 13 | 7/31 22:58:58 | 7/31 23:08:12 | 09:14 | 325.65 | SCE |

Day Ahead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS | Total |
| --- | --- | --- | --- | --- |
| Austin | 0 | 11 | 22 | 33 |
| Bryan Area | 0 | 0 | 4 | 4 |
| Corpus | 0 | 0 | 0 | 0 |
| DFW | 0 | 2 | 17 | 19 |
| E RIO | 0 | 0 | 1 | 1 |
| Houston | 0 | 0 | 3 | 3 |
| Laredo | 86 | 0 | 0 | 86 |
| North | 0 | 10 | 26 | 36 |
| Northeast | 0 | 0 | 0 | 0 |
| San Antonio | 0 | 0 | 8 | 8 |
| South | 0 | 5 | 2 | 7 |
| W RIO | 0 | 0 | 0 | 0 |
| Western | 0 | 0 | 0 | 0 |
|  | 86 | 28 | 83 | 197 |

| Historical Totals | July-06 | June-07 | July-07 |
| --- | --- | --- | --- |
| Austin | 32 | 65 | 33 |
| Bryan Area | 136 | 2 | 4 |
| Corpus | 13 | 2 | 0 |
| DFW | 76 | 3 | 19 |
| E RIO | 61 | 0 | 1 |
| Houston | 37 | 8 | 3 |
| Laredo | 94 | 90 | 86 |
| North | 46 | 12 | 36 |
| Northeast | 19 | 0 | 0 |
| San Antonio | 13 | 11 | 8 |
| South | 9 | 2 | 7 |
| W RIO | 111 | 0 | 0 |
| Western | 110 | 2 | 0 |
| Total | 757 | 197 | 197 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity (101)

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Temple - Tradinghouse & Temple Switch - Lake Creek 345 kV | Temple Pecan Creek - Lake Creek 138 kV | 9 |
| Garfield AEN - Onion Creek & Hicross AEN | Austrop 345/138 kV Auto | 8 |
| Enterprise-Trinidad & Martin Lake - Stryker Creek | Nacogdoches 345/138 kV Auto 1 | 7 |
| Lytton Springs - Zorn & Austrop - Zorn 345 kV | Canyon - Rohr 138 kV | 7 |
| Midland East - Odessa EHV 345 kV | Moss Switch - Odessa EHV 138 kV | 7 |
| Midland East - Odessa EHV 345 kV | Moss Switch - Odessa Southwest | 7 |
| Greenville Steam 138/69 kV Auto1 | Greenville Steam 138/69 kV Auto 2 | 4 |
| Sherry Switch - Everman Switch 345 kV | Bowen Tate Tap - Tate East Tap | 3 |
| North Denton 138/69 kV Auto 1 | North Denton 138/69 kV Auto 2 | 2 |
| Sandow Switch - Austrop 345 kV | Austrop 345/138 kV Auto | 2 |
| Stryker Creek 345/138 kV Auto | Walnut Grove - troup 138 kV | 2 |
| Magnesium Plant - Northland 138 kV | Pedernales - Burleson 138 kV | 2 |
| Calmont Switch - Benbrook Switch 138 kV | Eagle Mountain 345/138 kV Auto | 1 |
| Cagnon - Marbach Road 138 kV | Westside - Five Points 138 kV | 1 |
| Cagnon 345/138 kV Auto | Medical Center - Hamilton Wolfe | 1 |
| Duke - Pharr MVEC 138 kV | Duke - MVEC Palmhurst 138 kV | 1 |
| Duke - Pharr MVEC 138 kV | North Edinburg - Palmhurst 138 kV | 1 |
| Enterprise - Trinidad & Martin Lake- Stryker Ck | Nacogdoches South Tap - Nacogdoches 138 kV | 1 |
| Garfield- Onion Creek & Hicross | Lytton Springs 345/138 kV Auto | 1 |
| Gibbons Creek – Greens Prairie 138 kV | College Station Switch - Greens Prairie | 1 |
| Gibbons Creek - Greens Prairie and Gibbons Creek - East 138 kV | College Station Sw - Greens Prairie | 1 |
| Jewett - TH Wharton & Tomball | Macedonia - Seaway 138 kV | 1 |
| Sargent Road - Watermill 345 kV | Cedar Hill 345/138 kV transformer | 1 |
| South Bryan Swing - Bryan Greens Prairie | College Station Sw - Post Oak Sw | 1 |
| STP – Whitepoint 345 kV | Blessing - Lolita 138 kV | 1 |
| STP - Blessing 345 kV | Columbus - Stafford Hill 69 kV | 1 |
| Marion - Hill Country & Skyline 345 kV | Parkway - Schertz 138 kV | 1 |
| Wichita Falls #1 Auto | Wichita Falls - Wichita Falls Tap 69 kV | 1 |
| West Levee 345/138 kV #1 | West Levee 345/138 #2 | 1 |
| Comanche Peak-Decordova/Wolfhollow-Red Ck | Concord 345/138 kV Auto | 1 |
| Morgan Creek #1 Auto | Morgan Creek Auto #2 | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North - Houston | 10 |
| South - Houston | 6 |
| North - West | 4 |
| South - North | 2 |

New RAP (Date indicates last update of RAP not implementation date.)

6/01	Shamburger Tr and Martin Lake – Shamburger 345 MP

6/11	Temple Sw – Bell County 138 MP

6/12	Killeen Tr and Temple Sw – Killeen 345 kV MP

7/06	Duke – Pharr MVEC 138 kV PCAP

7/06	Macedonia – Seaway 138 kV PCAP

7/20	Greenville Steam Tr 1 and 2 MP

New Procedures/Forms/Operations Bulletins

| 07/26 | Transmission & Security Desk V3 Rev86 | 344 |
| --- | --- | --- |
| 07/26 | Day Ahead Desk V3 Rev33 | 343 |
| 07/26 | Frequency Control Desk V3 Rev 56 | 342 |
| 07/06 | Operating Period Desk V2 Rev 21 | 341 |
| 07/06 | Day Ahead Desk V3 Rev 32 | 340 |
| 07/06 | Shift Supervisor Desk R3 Rev 40 | 339 |
| 07/06 | Transmission & Security Desk V3 Rev 85 | 338 |
| 07/06 | Frequency Control Desk V3 Rev 55 | 337 |

## Blackout/Load Shed Incidences

None

EECP

8/1	Initiated EECP step 1 from 14:33 to 15:40

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

7/27	RPRS market failed for operating day 7/28.

Reliability frequency input project in Itest environment; potentially in production sometime in August.

Communication

7/18	RPRS Results for 7/19 operating day considered invalid.  Reran second RPRS study.

7/21	Held interval 16:30.  RTBM failed to clear.

7/25	Held interval 20:30.  RTBM failed to clear.

7/25	 IE 09:45 Balancing calculation was not captured.  A fail over was planned for 09:20 but was delayed until 09:35 due to a unit trip at 09:19.  Replication had been disabled in anticipation of the fail over and was not reset during the delay.

## ERCOT peak (Unofficial)

7/12 	17:00	56675

Yearly MTLF Error Comparison

| Month | MAPE for MTLF run at 16:00 Day Ahead (2005) | MAPE for MTLF run at 16:00 Day Ahead (2006) | MAPE for MTLF run at 16:00 Day Ahead (2007) |
| --- | --- | --- | --- |
| January | 5.02 | 4.79 | 4.55 |
| February | 3.47 | 4.81 | 3.75 |
| March | 3.41 | 4.95 | 2.70 |
| April | 3.37 | 5.59 | 3.002 |
| May | 4.21 | 3.59 | 3.220 |
| June | 3.91 | 2.65 | 4.460 |
| July | 5.22 | 2.62 | 4.29 |
| Average Annual MAPE | 4.56 | 3.79 | 3.71 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 7/2/07 | 16:35 | 18:06 | Advisory issued ARR below 3000 MW. |
| 7/3/07 | 13:08 | 18:30 | Advisory issued ARR below 3000 MW. |
| 7/3/07 | 14:28 | 18:30 | Alert issued ARR below 2500 MW. |
| 7/6/07 | 13:15 | 24:00 | Advisory issued ARR below 3000 MW. |
| 7/7/07 | 0:02 | 5:00 | Advisory issued ARR below 3000 MW. |
| 7/7/07 | 10:27 | 22:10 | Advisory issued ARR below 3000 MW. |
| 7/7/07 | 12:44 | 22:10 | Alert issued ARR below 2500 MW. |
| 7/8/07 | 14:36 | 20:10 | Advisory issued ARR below 3000 MW. |
| 7/9/07 | 13:46 | 18:25 | Advisory issued ARR below 3000 MW. |
| 7/10/07 | 15:40 | 19:10 | Advisory issued ARR below 3000MW. |
| 7/11/07 | 15:27 | 18:15 | Advisory issued ARR below 3000MW. |
| 7/12/07 | 15:10 | 19:54 | Advisory issued ARR below 3000MW. |
| 7/14/07 | 16:17 | 20:00 | Advisory issued ARR below 3000 MW. |
| 7/15/07 | 12:43 | 19:40 | Advisory issued ARR below 3000 MW. |
| 7/16/07 | 11:16 | 17:00 | Advisory issued ARR below 3000 MW. |
| 7/17/07 | 6:40 | 15:00 | OCN - Capacity insufficient for Hour Ending 16 and 17. |
| 7/17/07 | 10:40 | 22:05 | Advisory issued ARR below 3000 MW. |
| 7/18/07 | 21:00 | 23:00 | Alert issued to open an Adjustment Period Replacement Market. |
| 7/21/07 | 12:15 | 22:25 | Advisory issued ARR below 3000 MW. |
| 7/21/07 | 13:20 | 22:25 | Alert issued ARR below 2500 MW. |
| 7/22/07 | 3:00 | 11:15 | OCN issued - Capacity Shortage for hours 14:00 - 20:00. |
| 7/22/07 | 4:45 | 11:15 | Alert issued due to Capacity Shortage for hours 15:00 - 20:00. |
| 7/22/07 | 8:00 | 11:15 | Alert issued. Additional Replacement Reserves needed for Capacity Shortage. Opened Adjustment Period Replacement Market. |
| 7/22/07 | 12:35 | 20:59 | Advisory issued ARR below 3000 MW |
| 7/22/07 | 14:02 | 20:59 | Alert issued ARR below 2500 MW. |
| 7/23/07 | 12:35 | 17:32 | Advisory issued ARR below 3000 MW. |
| 7/23/07 | 14:30 | 17:32 | Alert issued ARR below 2500 MW. |
| 7/25/07 | 13:04 | 17:05 | Advisory issued ARR below 3000 MW. |
| 7/26/07 | 11:57 | 17:10 | Advisory issued ARR below 3000 MW. |
| 7/27/07 | 9:15 | 10:04 | Advisory issued ARR below 3000 MW. |
| 7/27/07 | 12:45 | 22:10 | Advisory issued ARR below 3000 MW. |
| 7/27/07 | 13:05 | 19:00 | Alert issued ARR below 2500 MW. |
| 7/27/07 | 23:05 | 24:00 | Advisory issued ARR below 3000 MW. |
| 7/28/07 | 0:15 | 1:45 | Advisory issued ARR below 3000 MW. |
| 7/28/07 | 10:27 | 24:00 | Advisory issued ARR below 3000 MW. |
| 7/28/07 | 12:50 | 18:30 | Alert issued ARR below 2500 MW. |
| 7/29/07 | 0:15 | 1:10 | Advisory issued ARR below 3000 MW. |
| 7/29/07 | 12:46 | 14:46 | Advisory issued ARR below 3000 MW. |
| 7/30/07 | 8:38 | 23:30 | Advisory issued ARR below 3000 MW. |
| 7/30/07 | 15:02 | 18:30 | Alert issued ARR below 2500 MW. |
| 7/31/07 | 9:52 | 20:05 | Advisory issued ARR below 3000 MW. |
| 7/31/07 | 14:48 | 18:40 | Alert issued ARR below 2500 MW. |

Transmission

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 7/16 | 2:15 | 7/18 12:00 | Transmission Emergency issued for the Laredo area . |
| 7/19 | 14:36 | 22:40 | Alert - Loss of North Denton Tr 1 loads Tr 2. |

Other

7/2 	19:32 Simultaneous loss of 2 units and 1 345 kV circuit.

7/31	11:00 Hillje project completed and energized, creating a new South to Houston CRE:  Hillje to WA Parrish 345 kV double circuit.