# ERCOT Independent Review

# ERCOT 2006 Five-Year Plan Project

# J.K. Spruce to Skyline Second 345 kV Circuit

# June 12, 2007

ERCOT Regional Planning

## Project Submitted

CPS Energy submitted a project for Regional Planning Group review in May 2007 for a project recommended in the 2006 ERCOT Five-Year Plan.  This project consists of the following elements; installing 345-kV line terminals and extending the 345-kV buses at Spruce and Skyline, and installing bundled 1271 AA conductor rated at 1446 MVA on the empty arm of the existing 345-kV double circuit towers between Spruce and Skyline.  The total estimated cost of this project is $7,750,000 with an anticipated in-service date of June 2009.  The project area is shown in figure 1.

Figure 1:  Project Area

## Project Justification

This project was found to be necessary and economic in the ERCOT 2006 Five-Year Plan and is recommended in the December 2006 Report on Existing and Potential Electric System Constraints and Needs document.  The most notable contingency is the 345 kV double circuit from Cagnon to Spruce and Cagnon to Von Rosenberg” which will cause the single circuit 345 kV line from Skyline to Spruce to be congested.  Adding a second circuit from Skyline to Spruce removes this congestion.

The congestion reduction effects from the addition of the second Skyline to Spruce circuit can be seen in the attached excel spreadsheet, “MCC report for 2009 2010 2011.xls”, in tabs for 2009 to 2011 marked “wo Skylspr”.  In the corresponding year tabs marked “w Skylspru” this congestion is not seen.

This project was re-evaluated using the latest 2006 Five-Year Plan cases for 2009 to 2011.  All the base cases were updated by adding Sandow unit 5 in the 2009 case, which was not in the earlier cases.  This study confirmed the project to be economic.  This project produces an estimated three year total production cost savings of $63.6 million over a three year period as shown in the table below.

The large increase in production cost savings in 2010 from 2009 is due to the addition of the Spruce 2 750 MW coal plant.

## Summary

ERCOT recommends this project and concurs with the analysis done by City Public Service Energy that originally classified this project as a reliability project to prevent overload of the existing Spruce to Skyline circuit 1 when Spruce unit 2 comes on-line in 2010.  The addition of this second circuit allows a more economic dispatch, prevents overload of the existing circuit, and the expected annual production cost savings should pay for this upgrade in less than two years.

## Designated Providers of Transmission Facilities

In accordance with ERCOT’s Power System Planning Charter and Processes, ERCOT staff is to designate transmission providers for projects reviewed in the regional planning groups.  These providers can agree to provide or delegate the new facilities or inform ERCOT they do not elect to provide them. For the project scope recommended in this report, CPS Energy is the sole provider of transmission facilities for this project.