## Slide 1: ROS Report to TAC
Randy Jones
August 2, 2007

## Slide 2: General Items
ROS has not met since the last TAC meeting
ROS approved OGRR202, Clarification of Responsibility for Switching of Transmission Elements via E-Mail
ROS will review new method for adjusting responsive reserves to trigger EECP events

## Slide 3: July 2nd LaaR Deployment
Three system elements lost (Trip times per PI data)
  19:31:56 Unit A trips at 830 MW
  19:32:10 Unit B trips at 113 MW
  19:32:30 345 kV Line C trips.
A total of 943 MW lost.

## Slide 4: July 2nd LaaR Deployment Action
850 MW of Responsive Reserve was deployed
At the time, event was considered a potential DCS event, call for LaaRs was initiated at 19:37. A total of 983 MW out of 1150 MW LaaRs deployed within the 10 minute initiation mark.
  Procedures indicate to deploy LaaRs for 950 MW of generation loss.
Frequency was at 59.942 Hz at the time the LaaR deployment call was initiated.

## Slide 5: July 2nd LaaR Deployment Results
Frequency recovered within 6 minutes of the disturbance.
Was later identified as a TRE Investigative Report due to the third element, 345 kV line tripping (initially not reported).
Not a DCS event, did not meet the 1083 MW loss requirement.

## Slide 6
? QUESTIONS ?