## Slide 1: PDCWG Report to ROS August 16, 2007
Bob Green
PDCWG Chair
Garland Power & Light

## Slide 2
ERCOT Frequency Control Performance to NERC CPS1 Standard (July ’07 unofficial)

## Slide 3
M
M
M
M

## Slide 4
M
M
M
M
M

## Slide 9: Activities
The PDCWG met on August 14 and 15.
The PDCWG continues to do some high level analysis of control performance during 0530 to 0630.
The WG continues to explore potential Nodal market control performance issues.
The WG is in the process of completing an update to the Disturbance Performance Summary for the first half of 2007.
The next meeting is September 11 and 12.

## Slide 10: Improvements to the process of bringing a unit on-line and ramping to full load
Presented to ROS by the PDCWG
August 2007

## Slide 14: Conclusions
Efforts to ramp a medium to large unit from off-line to full power over a ten minute period causes high frequency.
This creates the need for unnecessary deployments of Regulation Energy and contributes to poor ERCOT CPS1 scores.
Other units with governors back down [600 MW coal unit goes down 20MW@60.1hz].
The recommended practice is to schedule the ramp over several 15 minute intervals.