## Slide 1: LaaR Deployment – 7/2/07
Steve Krein
ERCOT Staff

## Slide 2: LaaR RRS Deployment on 7/2/07
Sequence of Events and System Summary
  ERCOT System loses about 1000 MW of Generation Resources at about 19:35
  Triggers a potential NERC Reportable DCS Event
  ERCOT Operator makes a hot line call to all QSEs
  VDI issued to deploy all LaaRs that are supplying RRS
  Eleven QSEs have LaaR RRS obligations which total 1150 MW
  Official start time for the deployment is 19:38:56 which coincides with the end of the Operator’s Instruction
  LaaR Response at 10 minute mark is 983 MW
  LaaRs reach 95% of system requirement at 12.5 minutes
  Total system response was 1184 MW

## Slide 3: LaaR RRS Deployment on 7/2/07

## Slide 4: LaaR RRS Deployment on 7/2/07
Compliance and System Operations Activities
  Five QSE portfolio responses meet 10 minute deployment criteria
  Incident Reports are issued to remaining six QSEs
  Compliance and System Operation Investigations are initiated with six QSEs
  Joint review of initial telemetry completed for all six QSEs on 7/16
  Review confirms that three QSEs failed to reach 95% of obligation in 10 minutes
  Remaining three QSEs will require additional review of IDR data
Next Steps?
  Complete Review and Prepare for Implementation of PRR714

## Slide 5: PRR714 – Modifications to LaaR Testing and Qualification
PRR Summary
  Requires Actual Interruption as part of Initial Qualification Test
  Requires an Unannounced Test of all UFR type LaaRs at least once every 365 days (actual deployment can be used in lieu of test)
  Defines conditions that would disqualify a LaaR from providing Ancillary Services

## Slide 6: PRR714 – Modifications to LaaR Testing and Qualification
Initial Qualification Test
  Major change is that simulated testing is no longer permitted
  LaaRs will be deployed and require an actual interruption of the Load
Annual Interruption Test
  ERCOT to work with QSEs to identify those LaaRs that require testing and to group LaaR deployments for each test
  LaaRs that have successfully deployed in last year may use those deployments in lieu of annual test
  Draft test procedure is under both internal and external review and will be distributed to Market Participants prior to start of testing
  LaaRs must be in the QSEs Resource Plan and shown as on-line and active with UFR enabled to be tested
  LaaR will receive a recall instruction at the end of the test and have three hours to recover before the QSE must replace or arrange for additional Resources

## Slide 7: PRR714 – Modifications to LaaR Testing and Qualification
Annual Interruption Test (cont.)
  While deployment may be done with a portfolio of LaaRs, evaluations will be made on an individual basis
  Any LaaR that responds with at least 95% of telemetered load value will be considered to have passed
  LaaRs that do not pass the test will be subject to additional tests
  LaaR Obligations for each QSE will be adjusted to reflect deployments and recovery period