## Slide 1: URL and HSL what is intent of protocol ROS August 16, 2007

## Slide 2
3.15 (4) Generation Resources required to provide VSS whose installations initially began operations on or after September 1, 1999, except as noted below, must have and maintain a URL which has an over-excited (lagging) power factor capability of 0.95 or less and an under-excited (leading) power factor capability of 0.95 or less, both determined at the generating unit's maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TSP.
Protocol Language

## Slide 3: Other Protocol defined terms
High Emergency Limit (HEL) - Limit established by the QSE describing the maximum temporary unsustainable energy production capability of the Resource. This limit must be achievable for a time stated by the QSE, but not less than 30 minutes.
High Sustained Limit-(HSL for a Generation Resource)- Limit established by the QSE, continuously updated in Real Time, that describes the maximum sustained energy production capability of the Resource.
Net Dependable Capability - The maximum sustained capability of a Resource as demonstrated by performance testing.
Unit Reactive Limit - The maximum quantity of Reactive Power that a Generation Resource is capable of providing at a 0.95 power factor at its maximum real power capability.

## Slide 4: URL and HSL
Armature
Current Constraint
Under
Excitation
Constraint
Field
Current Constraint
Unit
Reactive Limit (URL)
Maximum net power

## Slide 5: The Question
Is the “maximum net power to be supplied to the transmission grid” the HSL?
Is the language of protocol 3.15 (4) intended to limit the setting of HSL’s such that the intersection of .95 PF and the HSL fall within the CURL?