## Slide 1: Significant Events on June 18th, July 2nd, August 1st 2007
ERCOT Operations Support

## Slide 2: Events
June 18th EECP
July 2nd LaaR Deployment
August 1st EECP

## Slide 3: June 18th EECP
Implemented: 15:09
Terminated: 18:15

## Slide 4: June 18th EECP Root Causes
Day-Ahead Forecast discrepancy, short by 3,626 MW, 6.75%.
Total QSE’s SCE at the time of EECP implementation
-560 MW. ERCOT Load 52,370 MW.
The Day-Ahead forecast between the hours of 14:00 and 19:00 was low approximately by 4,6, and 5 degrees off Real-Time for the Coast, East, and North Central Weather Zones respectively.
  Zones expected to have cloudy skies and a potential for rain.

## Slide 5: June 18th EECP Action
Real-Time had to call for an additional 3,387 MW from what was seen in the Day-Ahead Online Capacity.
  OOMC Quick Start CTs
  DC Ties (East DC Tie, North DC Tie, Laredo VFT, and the Eagle Pass DC Tie)
There was no Non-Spinning Reserve (NSRS) requirement for that day.

## Slide 6: June 18th EECP Lessons
If there is sufficient time, ERCOT will make a better effort to use market tools, i.e. second Non-Spin market or a RPRS run during the Adjustment Period.
Procedures for DC Tie Schedules have been updated to improve communications and reflect NERC EEA Standards between SPP and ERCOT.
QSEs should not take units offline during EECP.
Non-Spin Reserves will be procured for days of questionable weather, i.e. chance of rain.

## Slide 7: July 2nd LaaR Deployment
Implemented: 19:37
Terminated: 20:06

## Slide 8: July 2nd LaaR Deployment Root Causes
Three system elements lost (Trip times per PI data)
  19:31:56 Unit A trips at 830 MW
  19:32:10 Unit B trips at 113 MW
  19:32:30 345 kV Line C trips.
A total of 943 MW lost.

## Slide 9: July 2nd LaaR Deployment Action
850 MW of Responsive Reserve was deployed
At the time, event was considered a potential DCS event, call for LaaRs was initiated at 19:37. A total of 983 MW out of 1150 MW LaaRs deployed within the 10 minute initiation mark.
  Procedures indicate to deploy LaaRs for 950 MW of generation loss.
Frequency was at 59.942 Hz at the time the LaaR deployment call was initiated.

## Slide 10: July 2nd LaaR Deployment Results
Frequency recovered within 6 minutes of the disturbance.
Was later identified as a TRE Investigative Report due to the third element, 345 kV line tripping (initially not reported).
Not a DCS event, did not meet the 1083 MW loss requirement.

## Slide 11: August 1st EECP
Implemented: 14:22
Terminated: 15:40

## Slide 12: August 1st EECP Root Causes
770 MW Unit A trip at 11:19 AM.
740 MW Unit B trip at 14:21 PM.
Day Ahead Load Forecast versus Real-Time Load was short only by 981 MW in the 15:00 1-Hour Average

## Slide 13: August 1st EECP Action and Lessons
1265 MW of Non-Spin Reserves were deployed at 14:30 requested at 14:07.
Requested assistance across DC Ties, North, East, Laredo, and Eagle Pass.
Procedures and Protocols were followed as intended.

## Slide 14: Questions?