## Slide 1: ERCOT DYNAMICS WORKING GROUP
Report to ROS August 16, 2007
Vance Beauregard, American Electric Power

## Slide 2: DWG – Report to ROS
The flat start with wind models continues, using PSS/e Rev. 30.3. This should be completed by the end of August.
The DWG discussed the Annual Dynamics Data Recorders determination. DWG recommends making no changes to the dynamics monitoring device (DDR) recommendations, which haven’t changed since March 2005.

## Slide 3: DWG – Report to ROS
The DWG reviewed the Oncor 600 MVAr Parkdale Dynamic Reactive project, and found that it is based on sound engineering and is worthy of ERCOT’s support.
We continue to discuss Voltage Recovery Criteria, in order to reach a resolution. New criteria were proposed using the concept of reactive margin testing. Members will investigate the impact on their systems.

## Slide 4: DWG – Report to ROS
The DWG discussed implementing the new Combined Cycle Models that have just been developed. The consultant converted the data for all of the combined cycle models in the ERCOT data, but there are opportunities to use the new models with the gas turbine units, in order to represent their frequency dependent behavior. Members will investigate this, and share issues they encounter in their own systems. We also discussed the use of the GGOV1 model, and other governor modeling issues.

## Slide 5: DWG – Report to ROS
The Procedure Manual will be updated. Members volunteered to take the manual by sections, and suggest revisions.
John Schmall will be making a presentation to a NERC Standards Drafting Team on the Underfrequency Loadshed studies and reports that DWG performed in 2001 and 2006.
The next DWG meeting has been tentatively set for September 26 & 27.

## Slide 6: DWG Tasks -- 2007
Task | Status
Flat start 2007 case | Complete
Flat start 2010 case | Complete
Flat start 2007 case with wind models. | Working
Publish 2006 flat start book. | Complete
Publish 2007 flat start book. | Working
Make annual determination of the number and location of dynamic monitoring devices. | Complete

## Slide 7: DWG Tasks -- 2007
Dynamic Voltage Recovery criteria | Working
Review recently approved NERC Standards with respect to ERCOT Op Guides and Protocols | Working
Participate in ROS Ad Hoc Task Force regarding Power System Stabilizers | Working
Annual Procedural Manual review/update | Working
Begin 2008 flat start activities | Fall Activity

## Slide 8: Review of Responsive Reserve Study
“Utilizing High-set Load Shedding Schemes To Provide Responsive Reserve Services”
DWG Report - November 2002

## Slide 9: Responsive Reserve - Study Results
Limit of interruptible load that can be used to replace Responsive Reserve
Results based on Sensitivity studies – Spring Off-Peak case:
 | Case 1 - 25% 575 MW High-set | Case 2 -50% 1150MW High-set | Case 3 -75% 1725 MW High-set | Case 4 -100% 2300 MW High-set
Level a: 59.7 Hz | Any | Any | <= 60 % (1380 MW) | N/A
Level b: 59.8 Hz | Any | Any | <= 40 % (920 MW) | N/A
Level c: 59.9 Hz | Any | Any | <= 55 % (1265 MW) | N/A

## Slide 10: Responsive Reserve - Conclusions
Can increase Interruptible to 1150 MW (50%)
Can increase to 1725 MW with limits on the amount of load in each of the frequency blocks
UFLS Stage 1 @ 59.3 Hz will trip for 2500 MW generation loss
Frequency overshoot can be avoided by limiting the amount of load in each of the frequency blocks

## Slide 11: Responsive Reserve - Recommendations
Increase present rule to allow 1150 MW (50%) to be met by interruptible load tripped at 59.9 Hz, 59.8 Hz, and 59.7 Hz.
Consider eventual increase to 1725 MW (75%) if no problems are noted with experience at 50%
Monitor the responsive load in real time.
Establish criteria for performance of generating units providing responsive reserve service.

## Slide 12: Issues for DWG Comment
What studies need to be completed before changes to RRS are considered?
What reliability concerns are raised by increasing LaaRs based upon 50% of a proposed new responsive reserve requirement of 2500 MW, or 2700 MW?

## Slide 13: Issues for DWG Comment
How much higher LaaR maximum limit would be possible if frequency tiered deployment were considered?
What has changed in key criteria/assumptions used in 2002 DWG study and do such changes indicate a need for an update of this study?

## Slide 14: Issues for DWG Comment
What would be involved in the way of a Responsive Reserve / LaaRs engineering study, and how long before any results would be known?

## Slide 15: DWG Comments
Frequency overshoot is the issue, when all load trips at a single frequency
If all load trips at one frequency, then 1150 MW is the limit.
If load shed is tiered, then 1725 MW is the limit for LaaRs.

## Slide 16: Changes in Key Assumptions
DWG 2002 study did not consider the amount or behavior of wind generation
Accuracy of relays is an issue
System inertia is less for off-peak and minimum conditions
More is known about the behavior and effective droop of generators

## Slide 17: Changes in Key Assumptions
New models are available for combined-cycle units, and the frequency-dependency of gas turbines can now be modeled
Load shedding frequency tier proposals may have changed (EILS)

## Slide 18: A new Responsive Reserve /LaaRs Study
Basic methodology from previous study can be used
Need to calibrate data to match governor response
Collect and review information concerning historical LaaR performance

## Slide 19: A new Responsive Reserve /LaaRs Study
If ROS provides guidance about the amount of RRS to use, it will simplify the studies, and reduce the complexity
More RRS values, potential LaaR values, more frequency tiers will take additional time and resources

## Slide 20: A new Responsive Reserve /LaaRs Study
Key DWG members are involved with other projects
Significant ERCOT staff time and computer resources will be required
ROS will need to make a request to ERCOT management to allocate the needed resources

## Slide 21: A new Responsive Reserve /LaaRs Study
A study scope will need to be prepared for ROS approval
It would be helpful if ROS would designate a representative to help narrow down the expectations and clearly define the scope for the study