ERCOT Operations Report

August 2007 ROS & OWG

Frequency Control

| Time | Freq(Hz) | Duration |  |
| --- | --- | --- | --- |
| 8/1 11:19:43 | 59.818 | 1 m 7 s | 790 MW trip |
| 8/1 14:20:56 | 59.854 | 55 s | 760 MW trip |
| 8/12 00:22:06 | 59.850 | 10 s | 590 MW trip |
| 8/14 11:01:44 | 60.124 | 8 m 54 s | Site failover caused STLF to be off by ~2000 MW. Offset was incorrect and the 11:15 interval was held. Some QSE continued to ramp to the 11:15 schedule. |
| 8/17 08:37:04 | 59.887 | 1 m 12 s | 350 MW trip |
| 8/19 23:12:28 | 59.868 | 12 s | 495 MW trip |
| 8/20 13:32:32 | 59.868 | 4 s | 650 MW trip |
| 8/22 07:01:54 | 59.892 | 6 s | 430 MW trip |
| 8/22 17:28:32 | 59.894 | 20 s | 520 MW trip |
| 08/25 00:49:16 | 59.884 | 2 m 26 s | 1860 MW wind scheduled, 940 MW wind generation |
| 08/25 04:05:12 | 60.107 | 28 s | 1075 MW total wind generation, total wind schedule dropped from 1315 to 685 across 04:00 ramp |
| 08/29 17:03:02 | 59.86 | 1m 2 s | 4 unit train trip totaling 820 MW |

Deployed Responsive (Reported Above)

| ID | Time of deployed | Stop Time | Duration | Max | Details |
| --- | --- | --- | --- | --- | --- |
| 1 | 8/1 11:19:43 | 8/1 11:34:48 | 0:15:05 | 773.38 |  |
| 2 | 8/1 14:20:54 | 8/1 14:31:20 | 0:10:26 | 590.21 |  |
| 3 | 8/12 0:22:06 | 8/12 0:29:18 | 0:07:12 | 610.57 |  |
| 4 | 8/14 11:37:50 | 8/14 11:49:00 | 0:11:10 | 320.54 | Overshoot of 11:00 event |
| 5 | 8/17 8:37:07 | 8/17 8:44:40 | 0:07:33 | 427.39 |  |
| 6 | 8/19 23:12:30 | 8/19 23:12:38 | 0:00:08 | 518.98 |  |
| 7 | 8/20 13:32:28 | 8/20 13:48:48 | 0:16:20 | 534.24 |  |
| 8 | 8/22 7:01:56 | 8/22 7:08:28 | 0:06:32 | 396.88 |  |
| 9 | 8/22 17:28:34 | 8/22 17:37:28 | 0:08:54 | 386.69 |  |
| 10 | 8/25 0:19:42 | 8/25 0:34:44 | 0:15:02 | 310.37 | Unit trip/SCE |
| 11 | 8/25 0:43:50 | 8/25 1:13:56 | 0:30:06 | 437.58 |  |
| 12 | 8/29 17:03:04 | 8/29 17:26:52 | 0:23:48 | 559.68 |  |

DayAhead OOMC and RMR Capacity Purchases

| Details | RMR | OOMC | RPRS | Total |
| --- | --- | --- | --- | --- |
| Austin | 0 | 10 | 6 | 16 |
| Bryan Area | 0 | 0 | 0 | 0 |
| Corpus | 0 | 0 | 1 | 1 |
| DFW | 0 | 8 | 15 | 23 |
| E RIO | 0 | 0 | 1 | 1 |
| Houston | 0 | 0 | 13 | 13 |
| Laredo | 92 | 0 | 0 | 92 |
| North | 0 | 8 | 83 | 91 |
| Northeast | 0 | 0 | 2 | 2 |
| San Antonio | 0 | 0 | 18 | 18 |
| South | 0 | 0 | 0 | 0 |
| W RIO | 0 | 0 | 0 | 0 |
| Western | 0 | 1 | 1 | 2 |
|  | 92 | 27 | 140 | 259 |

| Historical Totals | Aug-06 | Jul-07 | Aug-07 |
| --- | --- | --- | --- |
| Austin | 0 | 33 | 16 |
| Bryan Area | 86 | 4 | 0 |
| Corpus | 0 | 0 | 1 |
| DFW | 4 | 19 | 23 |
| E RIO | 12 | 1 | 1 |
| Houston | 0 | 3 | 13 |
| Laredo | 93 | 86 | 92 |
| North | 0 | 36 | 91 |
| Northeast | 0 | 0 | 2 |
| San Antonio | 0 | 8 | 18 |
| South | 0 | 7 | 0 |
| W RIO | 19 | 0 | 0 |
| Western | 17 | 0 | 2 |
| Total | 231 | 197 | 259 |

http://www.ercot.com/mktinfo/services/rprsdr/index.html

OOME and Congestion Management Activity

Congestion affected by outages

Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Temple - Tradinghouse & Temple Switch - Lake Creek 345 kV | Temple Pecan Creek - Lake Creek 138 kV | 18 |
| Enterprise - Trinidad & Martin Lake SES - Stryker Creek 345 kV | Nacogdoches 345/138 kV Auto 1 | 14 |
| Greenville Steam T1 138/69 kV | Greenville Steam T2 138/69 kV | 11 |
| Midland East - Odessa EHV 345 kV | Moss Switch - Odessa Southwest | 9 |
| West Denton 345/138 kV AT1 | Collin SES - Frisco 138 kV | 8 |
| Austrop 345/138 kV AT2 | Austrop 345/138 kV AT1 | 6 |
| Trinidad - Stryker Creek & Mt. Enterprise 345 kV | Stryker Creek - Cherokee 138 kV | 5 |
| Lytton Springs - Zorn & Austrop 345 kV | Canyon - Rohr 138 kV | 5 |
| Enterprise - Trinidad & Martin Lake SES - Stryker Creek 345 kV | Nacogdoches SE - Herty North Switch 138 kV | 5 |
| Gibbons Creek - Bryan Greens Prairie | College Station - Bryan Greens Prairie | 5 |
| Menard - Gillespie 138 kV | Menard 138/69 kV AT1 | 4 |
| Morgan Creek 345/138 kV AT1 | Morgan Creek 345/138 kV AT2 | 3 |
| Bluff Creek - San Angelo Red Creek | Bluff Creek - Abilene Mulberry Creek | 3 |
| North Denton 138/69 kV AT1 | North Denton 138/69 kV AT2 | 3 |
| Fort Mason 138/69 kV AT1 | Menard 138/69 kV AT1 | 2 |
| La Sierra - Hill Country 138 kV | Medical Center - Hamilton Wolfe 138 kV | 2 |
| Snyder - Sun Switch 138 kV | Ennis Creek Switch 138/69 kV AT1 | 2 |
| Anna Switch - Farmersville & Valley South | Anna Switch - Collin 345 kV | 1 |
| Austrop - Daffin & Decker 138 kV | Garfield AEN - Hicross AEN 138 kV | 1 |
| Brownwood - Goldthwaite 138 kV | Killeen Switch - Killeen Fort Hood Switch | 1 |
| Carrollton North West - Collin 345 kV | Allen Switch - Plano Custer Road 138 kV | 1 |
| Duke - Aderhold 138 kV | Hall Acres - South McAllen 138 kV | 1 |
| Duke - Pharr 138 kV | North Edinburg - Palmhurst 138 kV | 1 |
| Everman Switch-Decordova & Rocky Creek | Decordova - Benbrook Sw | 1 |
| Graham - Sweetwater Cogen & Long Creek | Abilene South - Potosi Tap 138 kV | 1 |
| Hill Country - Hellotes 138 kV | Medical Center - Hamilton Wolfe 138 kV | 1 |
| Holly - Barney Davis 138 kV | Cabaniss - Westside 138 kV | 1 |
| Industrial - Denton Arco 138 kV | Hickory Denton - North Lake Denton 69 kV | 1 |
| Morgan Creek - Quail Switch & Odessa | Midland East - Big Springs West 138 kV | 1 |
| PH Robinson - Southshore 138 kV | Dickenson - League City 138 kV | 1 |
| Trinidad - Stryker Creek & Mt. Enterprise | Athens North - Athens Tap 138 kV | 1 |
| Trinidad - Stryker Creek & Mt. Enterprise | Elkton 345/138 kV AT1 | 1 |
| Lake Creek SES - Jewett 345 kV | Jewett - Seaway Teague Tap 138 kV | 1 |
| Marion - Hill Country & Skyline 345 kV | Schetz - Parkway 138 kV | 1 |
| Airline - Westside 138 kV | Barney Davis - Rodd Field 138 kV | 1 |

Zonal OC1

| CSC | Days |
| --- | --- |
| North - West | 5 |
| North - Houston | 4 |
| West - North | 2 |
| South - North | 1 |

New RAP

08/01	Jewett – Lake Creek 138 kV Mitigation Plan

08/09	Dilley Sw – San Miguel 138 kV Mitigation Plan

08/15	PH Robinson – South Shore 138 kV Mitigation Plan

08/22	Fort Mason Transformer Mitigation Plan

New Procedures/Forms/Operations Bulletins

8/06	POB 345 – Frequency control Desk

## Blackout/Load Shed Incidences

None

EECP

8/1	Initiated EECP step 1 from 14:33 to 15:40

Major System Voltage Problems

None

Major Computer Problems, Enhancements & Fixes

8/23	Frequency input reliability enhancement project in production.

Communication

8/14	Held 11:15 interval.  Offset error

8/23 	Held 09:00 interval.  Offset error

8/31	18:55 – 9/1 00:25	Loss of communication (SCADA, RTU, telephone) with TO/QSE when lightning struck a microwave tower at the control center.

## ERCOT peak (Unofficial)

8/13	17:00	62,100

Yearly MTLF Error Comparison

| Month | MAPE for MTLF run at 16:00 Day Ahead (2005) | MAPE for MTLF run at 16:00 Day Ahead (2006) | MAPE for MTLF run at 16:00 Day Ahead (2007) |
| --- | --- | --- | --- |
| January | 5.02 | 4.79 | 4.55 |
| February | 3.47 | 4.81 | 3.75 |
| March | 3.41 | 4.95 | 2.70 |
| April | 3.37 | 5.59 | 3.002 |
| May | 4.21 | 3.59 | 3.220 |
| June | 3.91 | 2.65 | 4.460 |
| July | 5.22 | 2.62 | 4.29 |
| August | 4.86 | 2.09 | 3.11 |
| Average Annual MAPE | 4.56 | 3.79 | 3.64 |

OCN, Advisory, Alerts & Emergency Notices

Capacity

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 8/1 | 7:18 | 18:00 | OCN for capacity issued, load 1000 MW ahead of forecast |
| 8/1 | 12:46 | 18:04 | Advisory issued ARR below 3000 MW. |
| 8/1 | 14:04 | 17:00 | Alert issued ARR below 2500 MW. |
| 8/1 | 14:22 | 15:40 | EECP Step 1 Declared. ARR below 2300 MW. |
| 8/3 | 12:35 | 18:14 | Advisory issued ARR below 3000 MW. |
| 8/5 | 14:09 | 18:58 | Advisory issued ARR below 3000 MW. |
| 8/6 | 15:53 | 17:23 | Advisory issued ARR below 3000 MW. |
| 8/7 | 13:40 | 19:00 | Advisory issued ARR below 3000 MW. |
| 8/8 | 14:40 | 18:45 | Advisory issued ARR below 3000 MW. |
| 8/9 | 14:06 | 18:45 | Advisory issued ARR below 3000 MW. |
| 8/10 | 13:23 | 14:11 | Advisory issued ARR below 3000 MW. |
| 8/10 | 15:40 | 17:45 | Advisory issued ARR below 3000 MW. |
| 8/11 | 15:33 | 18:15 | Advisory issued ARR below 3000 MW. |
| 8/12 | 13:19 | 19:05 | Advisory issued ARR below 3000 MW. |
| 8/12 | 13:30 | 19:05 | Alert issued ARR below 2500 MW. |
| 8/12 | 21:00 | 23:00 | OCN issued for capacity shortage for hours 16:00 to 18:00. |
| 8/13 | 1:25 | 11:40 | Alert issued for capacity shortage for hours 16:00 to 18:00. |
| 8/13 | 14:32 | 18:10 | Advisory issued ARR below 3000 MW. |
| 8/14 | 14:35 | 18:50 | Advisory issued ARR below 3000 MW. |
| 8/15 | 12:50 | 18:04 | Advisory issued ARR below 3000 MW. |
| 8/17 | 8:08 | 19:20 | Advisory issued ARR below 3000 MW. |
| 8/17 | 12:26 | 18:30 | Alert issued ARR below 2500 MW. |
| 8/18 | 15:18 | 20:10 | Advisory issued ARR below 3000 MW. |
| 8/19 | 13:11 | 22:15 | Advisory issued ARR below 3000 MW. |
| 8/19 | 15:00 | 22:10 | Alert issued due ARR below 2500 MW. |
| 8/20 | 12:58 | 18:30 | Advisory issued ARR below 3000 MW. |
| 8/20 | 13:34 | 18:30 | Alert issued ARR below 2500 MW. |
| 8/21 | 13:30 | 16:30 | OCN issued for shortage of UBES bids for HE 1600 - 1800. |
| 8/21 | 14:06 | 18:05 | Advisory issued ARR below 3000 MW. |
| 8/21 | 14:59 | 18:05 | Alert issued ARR below 2500 MW. |
| 8/22 | 7:13 | 9:00 | Advisory issued ARR below 3000 MW. |
| 8/23 | 13:46 | 19:15 | Advisory issued ARR below 3000 MW. |
| 8/23 | 14:25 | 18:33 | Alert issued ARR below 2500 MW. |
| 8/24 | 13:35 | 18:00 | Advisory issued ARR below 3000 MW. |
| 8/24 | 13:50 | 18:00 | Alert issued ARR below 2500 MW. |
| 8/26 | 15:20 | 18:00 | Advisory issued ARR below 3000 MW. |
| 8/26 | 16:10 | 18:00 | Alert issued ARR below 2500 MW. |
| 8/26 | 18:42 | 19:13 | Advisory issued ARR below 3000 MW. |
| 8/27 | 15:14 | 17:15 | Advisory issued ARR below 3000 MW. |
| 8/28 | 15:25 | 18:09 | Advsiory issued ARR below 3000 MW. |
| 8/30 | 12:25 | 19:12 | Advisory issued ARR below 3000 MW. |
| 8/31 | 12:00 | 18:10 | Advisory issued ARR below 3000 MW. |
| 8/31 | 19:33 | 22:18 | Advisory issued ARR below 3000 MW |

Transmission

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 8/13 | 11:00 | 24:00 | Transmission Alert - Denton area due to forced outages. |
| 8/14 | 0:15 | 12:45 | Transmission Alert - Denton area due to forced outages. |
| 8/14 | 15:03 | 24:00 | Transmission Alert - Loss of West Denton 345/138 kV T1 loads Collin - Frisco |
| 8/15 | 0:15 | 24:00 | Transmission Alert. Loss of West Denton 345/138 kV T1 loads Collin - Frisco. |
| 8/15 | 16:00 | 21:30 | Transmission Alert.Loss of Lake Creek - Jewett 345 kV loads Jewett - Seaway Teague Tap 138 kV. |
| 8/16 | 0:15 | 9:10 | Transmission Alert. Loss of West Denton 345/138 kV T1 loads Collin - Frisco. |
| 8/23 | 7:30 | 10:16 | Transmission Alert. Loss of Oklaunion - Fisher Road Switch - Bowman 345 kV loads Lake Pauline - Vernon 138 kV. |

Weather

| Date | Start | End | Details |
| --- | --- | --- | --- |
| 8/12 | 12:40 | 24:00 | OCN Heat advisory for the ERCOT region for 08/13/07. |
| 8/13 | 0:15 | 24:00 | OCN Heat advisory for the ERCOT region for 08/13/07. |
| 8/14 | 0:15 | 24:00 | OCN Heat advisory for the ERCOT region for 08/14/07. |
| 8/15 | 0:15 | 11:02 | OCN Heat advisory for the ERCOT region. |
| 8/15 | 15:00 | 24:00 | OCN for wet weather |
| 8/16 | 0:15 | 24:00 | OCN for wet weather -Tropical Storm Erin |
| 8/17 | 0:15 | 24:00 | OCN for wet weather -Tropical Storm Erin |
| 8/18 | 0:15 | 6:00 | OCN for wet weather -Tropical Storm Erin |

Other

8/12 	10:39	Simultaneous loss of a unit, transformer and 57 MW load in the North Zone.

8/27 	06:40	Simultaneous loss of a 138 kV circuit and 3 units totaling 43 MW.

8/29	17:03	Simultaneous loss of a 345 kV circuit and a 4-unit train.