ERCOT OPERATIONS REPORT

ON THE

DCS AND EECP EVENT

SEPTEMBER 5, 2007

Executive Summary..............................................................................................................3

Time Line and Description of Significant Events.................................................................4

Observations/Data Review....................................................................................................5

LOAD, ARR, AND RRS								5

DISTURBANCE FREQUENCY AND RRS DEPLOYED				6

RAW SCADA LAAR PERFORMANCE						7

TOTAL SCE AND FREQUENCY							8

FREQUENCY AND REGULATION						9

Lessons Learned....................................................................................................................10

### Executive Summary

ERCOT implemented Step One of its Emergency Electric Curtailment Plan (EECP) on

September 5, 2007.  Factors that led to ERCOT implementing the EECP Step One:

Prior to the implementation of EECP, Units A and B tripped at a total of 1084 MW at 7:52 AM as well as the loss of two 345 kV circuits.  This event qualified as a Disturbance Control Standard (DCS) event.  Frequency recovered to 60 Hz in six minutes and eight seconds, not violating the DCS criteria.

Call for LaaR deployment was initiated at 7:57:57.  SCADA results show that 1068 MW of LaaR was deployed within the 10 minute mark including the LaaRs deployed at 59.8 Hz.

At 8:04 AM EECP was implemented due to Adjusted Responsive Reserve (ARR) dropping below 2300 MW.  ARR initially dropped to 1932 MW and recovered to

2268 MW.  Prior to disturbance load pick up was 1500 MW/hr.

Quick start generation units were called for until 11:00.  Emergency power was not available during the event over the DC Ties.  There were no requirements for non-spin at the time.

EECP Step 1 was terminated at 9:33.

### Time Line and Description of Significant Events

- 1:00  	Advisory issued ARR below 3000 MW.  Actual at 2881 MW.

- 6:17	Frequency dropped 59.91 Hz due to heavy load pick up load.  Actual load was

35,111 MW.  Deployed 315 MW of responsive reserve (RRS).  Load was rising at 1500 MW/hr.

- 7:52 	Two 345 kV circuits tripped and Units A and B tripped at a total of 1084 MW.

Frequency dropped to 59.739 Hz.  High winds and a possible tornado were reported in the area.  Deployed 1162 MW of RRS.

- 7:52  	High set LaaR deployed due to frequency below 59.8 Hz.

- 7:57  	ERCOT issued LaaR deployment at 07:57:57 due to DCS event.

- 08:00	Alert issued ARR below 2500 MW.  Actual at 2368 MW.

- 08:04	Issued EECP Step 1 due to ARR below 2300 MW.  ARR initially dropped to

1932 MW and recovered to 2268 MW.

- 08:10	QSE reports that North DC Tie tripped off line with 64 MW flowing out of

ERCOT, they are investigating the cause.

- 08:15	OOME VDI Units C, D, E, F, G, H & I.

- 08:29 – 8:40

  - Requested emergency power from DC Ties.  Emergency power was not available.

- 08:31	OOMC GTs J, K, L, M, N, O, P, & Q.

- 09:15	Started calling QSEs individually to restore LaaRs at 09:15 and finished

approximately 09:26 with request to fully restore LaaRs.

- 09:33	EECP Step 1 terminated.  ARR is at 3395 MW.

- 09:34	Called SPP and informed them that ERCOT cancelled EECP Step 1.

- 11:00	Ended all OOMC/OOME quick start generation.

### Observations/Data Review

09/05/07 07:00 – 10:00 LOAD, ARR, AND RRS

09/05/07 7:50 – 9:30 DISTURBANCE FREQUENCY AND RRS DEPLOYED

Pre-disturbance frequency = 60.003 Hz

09/05/07 7:37 – 8:37 RAW SCADA LAAR PERFORMANCE

09/05/07 07:00 – 10:00 TOTAL SCE AND FREQUENCY

09/05/07 07:00 – 10:00 FREQUENCY AND REGULATION

### Lessons Learned

- LaaR deployment and RRS deployment recovered frequency without violating the Disturbance Control Standards.

- NERC report EOP-004 was filed for the DCS Event.