| NPRR Number | 081 | NPRR Title | Automatic Voltage Regulator (AVR) Status |
| --- | --- | --- | --- |
| Date |  | 09/10/07 |  |
| Submitter’s Information |  |  |  |
| Name |  | Trip Doggett on behalf of the Transition Plan Task Force (TPTF) |  |
| E-mail Address |  | tdoggett@ercot.com |  |
| Company |  | ERCOT |  |
| Phone Number |  | 512-248-6360 |  |
| Cell Number |  |  |  |
| Market Segment |  | N/A |  |

| Overall Market Benefit |  |
| --- | --- |
| Overall Market Impact |  |
| Consumer Impact |  |

| ERCOT/Market Segment Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions |  |  |  |
|  |  | Impact Area | Monetary Impact |
| Market Cost |  | Unknown | Unknown |
|  |  | Impact Area | Monetary Impact |
| Market Benefit |  | Facilitates compliance with NERC Reliability Standards | Unknown |
| Additional Qualitative Information |  |  |  |
| Other Comments |  |  |  |

Comments

On September 10, 2007, the TPTF approved the comments indicated below for Section 3.15.3, QSE Responsibilities Related to Voltage Support, Paragraph (4), to be submitted to Market Rules and forwarded to PRS.  These comments recommend:

1.) 	Providing QSEs with a thirty-minute window wherein to telemeter AVR statuses to ERCOT following any change in operational mode; and

2.) 	Striking the phrase, “When the QSE changes mode, the QSE shall promptly inform ERCOT.”

The TPTF recommends that QSEs should not be required to communicate any change in operational mode to ERCOT through other means additional to the required telemetry.

Revised Proposed Nodal Protocol Language

3.15.3	QSE Responsibilities Related to Voltage Support

(1)	QSE Generation Resources required to provide VSS shall have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the ERCOT Operating Guides.

(2)	QSE Generation Resources providing VSS shall be compliant with the ERCOT Operating Guides for response to transient voltage disturbance.

(3)	QSE Generation Resources providing VSS must meet technical requirements specified in Section 8.1.2.1, Ancillary Service Qualification and Testing, and the performance standards specified in Section 8.1.2, QSE Ancillary Service Performance Standards.

(4)	Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) in the voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is going On-Line or Off-Line or the QSE determines a need to operate in manual mode in Emergency Conditions.  Each QSE shall, within 30 minutes of a change in the operational mode of the AVR, send to ERCOT via telemetry the AVR status of each Generation Resource providing VSS.  An “On” status will indicate the AVR is on and set to regulate the Resource’s terminal voltage in the voltage control mode and an “Off” status will indicate the AVR is off or in a manual mode.  . Any QSE-controlled power system stabilizers must be kept in service unless specifically permitted to operate otherwise by ERCOT.  Each QSE shall monitor the status of their regulators and stabilizers, and shall report abnormal status changes to ERCOT.

(5)	Each QSE shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits.

(6)	The reactive capability required must be maintained at all times that the Generation Resource is On-Line.