## Slide 1
Abilene
Mc Camey
Big Spring

## Slide 2
Far West

## Slide 3: Abilene Area All the values are based on returned ERCOT survey results
Total number of Wind Powered Generation Resources (WPGR) 16 (7)
Total max rated capacity – 970 MW Average rated capacity – 139 MW
Average cut-off speed – 59 MPH
Average minimum wind speed at which generation starts – 8 MPH
Total rated reactive capability – 396 MVAr
Dynamic VAr control – 57% and Static VAr control – 43 %
Average number of turbines at each plant site – 92
43 % of the units in this area have feathering of the blades to control the output level (Based on the survey responses).

## Slide 4: Big Spring Area All the values are based on returned ERCOT survey results
Total number of WPGR’s 7 (7)
Total max rated capacity – 624 MW Average rated capacity – 104 MW
Average cut-off speed – 56 MPH
Average minimum wind speed at which generation starts – 9 MPH
Total rated reactive capability – 181 MVAr
Dynamic VAr control – 43% and Static VAr control – 57 %
Average number of turbines at each plant site – 80
26 % of the units in this area have feathering of the blades to control the output level (Based on the survey responses).

## Slide 5: McCamey Area All the values are based on ERCOT returned survey results
Total number of WPGR’s 10 (2)
Total max rated capacity – 321 MW Average rated capacity – 161 MW
Average cut-off speed – 56 MPH
Average minimum wind speed at which generation starts – 8 MPH
Total rated reactive capability – 200 MVAr
Both the units have dynamic VAr control
Average number of turbines at each plant site – 107
All the units have feathering of the blades to control the output level (Based on the survey responses).

## Slide 6
Region | Abilene (MVAr) | Big Spring (MVAr) | McCamey (MVAr)
Avg. Reactive Capability at 50% O/P | 27.105 | 10.788 | 40
Avg. Reactive Capability at 100% O/P | 36.57 | 15.775 | 100
Avg. Reactive Capability at no O/P | 2.5 | 6.029 | 0

## Slide 7: What is the VAR Capability required in the Interconnection Agreement?
Abilene: 3 units said 0.95 leading or lagging Power factor.
4 said none.
Big Spring: All the units said 0.95 leading or lagging Power factor
McCamey: None

## Slide 8: How far can units be backed down before operation becomes unstable (MW output or % of rated capability)?
Region | Abilene MW | Big Spring MW | McCamey MW
MW output after which operation becomes unstable | 0.086 | 0.057 | 0

## Slide 9: Can individual turbines of this type be shut down at the facility on a routine basis (stop and start once per day)?
Abilene: 6 WPGR’s have the capability and 1 does not.
Big Spring: 7 WPGR’s have the capability of shutting individual turbines at the facility on a routine basis.
McCamey: Both respondents said that current control scheme does not shut down turbines but limit power output by modulating blade pitch.

## Slide 10: Are the facility turbines and control system and facility turbines able to provide automatic generation control (AGC) from a technical point of view? If not, would the turbines be capable of this if the control system was upgraded?
Abilene: None in Abilene area can provide AGC.
Big Spring: 6 in Big Spring cannot provide automatic generation control (AGC). 1 can.
McCamey: 1 in McCamey area can provide Automatic Voltage Control whose set point is controlled by ERCOT.

## Slide 11: How flexible is the zero output reactive capability? For example, is it manually or automatically switched in? What are the issues associated with provided this reactive capability if requested by ERCOT in Real Time.
Abilene: 3 have static reactive capability, which is only capacitive reactive compensation that can be controlled manually or automatically. 3 cannot provide any flexibility. 1 WPGR’s VAr output is attributed to the capacitive nature of the underground collection system. Capability is limited due to underground cable splices and thermal backfill material.
Big Spring Area: 5 cannot have any flexible reactive capability at zero output. 1 has manual switching capability. 1 has static reactive capability, which is only capacitive reactive compensation that can be controlled manually or automatically.
McCamey: None in McCamey area have flexible reactive capability at zero output.

## Slide 12
What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
Abilene:
Under voltage - 299vac at the turbine. Over voltage - 365vac at the turbine. Over frequency - 61hz at the turbine. Under frequency - 59hz at the turbine. 25vac asymmetry between phases at the turbine for 3 WPGR’s
Voltage 110 % nominal or < 70 % nominal for 1 WPGR
No response from 3 WPGR’s

## Slide 13: What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
Big Spring Area:
90% ≤ System Voltage ≥ 110% ; 94% ≤ System Frequency ≥ 104% is the response from 2 WPGR’s
For a V-47 and a V-66 WTGL high voltage 500V sensed phase to ground, low voltage 340V sensed phase to ground; For a V-47: high frequency 60.4hz, low frequency 59.2hz; For a V-66: high frequency 60.3hz, low frequency 59.5hz.
Over Freq>61Hz for 0.5 s, Under Freq <=59 Hz Over Volt>120%
Breaker trip for 2 WPGR’s

## Slide 14
What ERCOT electric system conditions can cause machines to trip offline and what are the corresponding set points?
McCamey:
Voltage 110 % nominal or < 70 % nominal for 1 WPGR for both WPGR’s

## Slide 15: What is the response time required to reduce output by 20%? (time from ERCOT notice to reduce to time when wind-ranch is 20% below previous output)?
Average response time for 4 WPGR’s in Abilene is 6.25 min. 3 have a response of “This is not the way the system operates, the turbines are turned off in groups to reduce the maximum MW output - it does not "set" output.”
Average response time for Big Spring is 24 min.
Average response time for McCamey is 10 min

## Slide 16: What is the response time required to increase output by 20% (presuming wind available)? (time from ERCOT notice to increased to time when wind-ranch is 20% above previous output?
Average response time for 4 WPGR’s in Abilene is 6.25 min. 3 have a response of “This is not the way the system operates, the turbines are turned back on in groups to reduce the maximum MW output - it does not "set" output.”
Average response time for 5 WPGR’s Big Spring is 21 min.3 WPGR’s have a response of “This is not the way the system operates, the turbines are turned back on in groups to reduce the maximum MW output - it does not "set" output.”
Average response time for McCamey is 10 min

## Slide 17: When turbines are being controlled what is the available ramping capability assuming wind conditions and system transmission conditions that could accommodate full output? (ERCOT seeks to understand the ramping characteristics of the units and facility as a whole). Please describe (or provide output curves) on facility ramp rates and wind speed? (i.e. How long would it take to go from zero to 25% output? How long to go from 25 to 50% output? How long from 50 to 75% output and from 75% to 100% output?) Is the wind farm operating as designed? If not, why not?
Abilene: 0-25% (375kw) less than 1 minute;25-50% (750kw) less than 1 minute; 50-75% (1,125kw) less than 1 minute; 75-100% (1,500kw) less than 1 minute; 0-100% (1,500kw per unit) less than 4 minutes
Big Spring: There are no ramp rates. Everyone answered wind is the deciding factor for the output.
McCamey: 1 WPGR’s response is “Individual turbine can modulate from very low load levels to full load in about 2.5 minutes. Entire farm can modulate in about 5 minutes dependent on wind at each individual turbine location”.