| NOGRR Number | 010 | NOGRR Title | Nodal Operating Guides - Section 8 - Attachment C, Turbine Governor Speed Tests |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approval |
| Nodal Operating Guide Section Requiring Revision |  | Section 8 - Attachment C, Turbine Governor Speed Tests |  |  |
| Proposed Effective Date |  | ## Upon Texas Nodal Market implementation. |  |  |
| Revision Description |  | This Nodal Operating Guide Revision Request (NOGRR) proposes language for Section 8, Attachment C of the Nodal Operating Guides. |  |  |
| Overall Market Benefit |  | Continuity of Nodal Operating Guides with Nodal requirements. |  |  |
| Overall Market Impact |  | To be determined. |  |  |
| Consumer Impact |  | Unknown. |  |  |
| Credit Implications |  | No. |  |  |
| TPTF Review |  | On 08/14/07, TPTF reviewed NOGRR001 – NOGRR017. No comments were received on this NOGRR. |  |  |
| Procedural History |  | - On 06/21/07, NOGRR010 was posted. - On 07/17/07, the Operating Guides Revision Task Force (OGRTF) comments were posted. - On 07/18/07, the Operations Working Group (OWG) considered NOGRR010. - On 08/17/07, the Impact Analysis (IA) was posted. - On 08/22/07, the OWG considered the OWG Recommendation Report and IA. - On 09/13/07, the ROS considered this NOGRR. |  |  |
| OWG Recommendation |  | On 07/18/07, the OWG was in consensus to recommend approval of NOGRR010 as submitted. On 08/22/07, the OWG was in consensus to forward the OWG Recommendation Report and IA to ROS for approval. |  |  |
| Summary of OWG Discussion |  | On 07/18/07, the OWG discussed OGRTF’s methodology in developing NOGRR001-017. Please see OWG discussion points below. On 08/22/07, there was no discussion. |  |  |
| ROS Recommendation |  | On 09/13/07, the ROS voted unanimously to recommend approval of this NOGRR as recommended by the OWG. All Market Segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | On 09/13/07, there was no discussion. |  |  |

| ERCOT/Market Segment Impacts and Benefits |  |  |  |
| --- | --- | --- | --- |
| Assumptions | 1 | Impacts of Nodal Operating Guides are encompassed by the Nodal Protocols |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Cost | 1 | Unknown |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Market Benefit | 1 | Continuity of Operating Guides with Nodal Protocols |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Additional Qualitative Information | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |
| Other Comments | 1 |  |  |
|  | 2 |  |  |
|  | 3 |  |  |
|  | 4 |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | Stephen C. Knapp on behalf of the Operating Guides Revision Task Force (OGRTF) |
| E-mail Address | Steve.knapp@constellation.com |
| Company | Constellation Energy Commodities Group, Inc. |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| OGRTF 071707 | Proposed that OWG recommend approval of NOGRR010 as submitted. |

OWG Discussion Points

The main objective of the OGRTF in developing NOGRR001-017 was to bring the current Operating Guides into alignment with Nodal requirements.  The OGRTF recognizes that there may be other issues that need to be addressed through the NOGRR process and invites Market Participants to submit NOGRRs to resolve these issues after NOGRR001-017 have been approved.  The following are concepts and assumptions used by the OGRTF in developing the NOGRRs:

- Unapproved NPRRs and OGRRs have not been included in this release

- Terminology Changes:

  - “ERCOT Compliance” changed to “Texas Regional Entity” as appropriate

  - “Control Area Authority” changed to “ERCOT”

  - “LaaRs” changed to “Load Resources”

  - The term “ERCOT” can apply to ISO, Compliance, Planning, Engineering, etc.

  - Kept existing ERCOT Entity Names and Acronyms in lieu of incorporating NERC terminology

- Format Changes:

  - Removed Protocol Excerpts

  - Test Forms and Support Documents moved to Section 8, Attachments

  - Consolidated testing and compliance in Section 3, Resource Testing and Qualification Procedures

  - Definitions, including “Credible Single Contingency,” moved to Section 1, Overview

Proposed Nodal Operating Guide Language Revision

ERCOT Nodal Operating Guides

Section 8

Attachment C

Turbine Governor Speed Tests

(Effective Upon Texas Nodal Market Implementation)

# Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

General Information

Unit Code (16 character):   			Location (County) :

Unit Name:  					Date of test:

QSE:						Resource Entity:

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM |  |  |  |  |  |  |
| Frequency Hz |  |  |  |  |  |  |

Speed Changer Travel Time:

(a)	From Low-Speed Stop to High-Speed Stop in _________seconds.

(b)	From High-Speed Stop to Low-Speed Stop in _________seconds.

Over-speed Trip Test Speed at _________rpm.

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Rep.:

# Example of a Turbine Governor Speed Regulation Test for Mechanical-Hydraulic Governor

Steady State Speed Regulation at High-Speed Stop

Rs=A−B×1003600=3850−3570×1003600=7.78%

Where:

A =	Speed with speed changer set at high-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

B =	Speed with speed changer set at high-speed stop and when governing valves just reach wide-open position.

Steady State Speed Regulation at Synchronous Speed

Rs=C−D×1003600=3600−3310×1003600=8.06%

Where:

C =	Speed with speed changer set for synchronous speed and with throttle (or stop) valves open and machine running idle on the governor.

D =	Speed with speed changer set at the same position as in C above and when governing valves just reach wide open position.

Steady State Speed Regulation at Low-Speed Stop

Rs=E−F×1003600=3500−3210×1003600=8.06%

Where:

E =	Speed with speed changer set at low-speed stop and with throttle (or stop) valves open and machine running idle on the governor.

F =	Speed with speed changer set at low-speed stop and when governing valves just reach wide-open position.

E, F @ Low Speed Stop

C, D @ Sync. Speed

A, B @ High Speed Stop

Test Data

| Point | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Speed, RPM | 3850 | 3570 | 3600 | 3310 | 3500 | 3210 |
| Frequency Hz | 64.2 | 59.5 | 60.0 | 55.0 | 58.3 | 53.5 |

Speed Changer Travel Time:

a.	From Low-Speed Stop to High-Speed Stop in 	73	seconds.

b.	From High-Speed Stop to Low-Speed Stop in 	74	seconds.

Over-speed Trip Test Speed at 	3965	rpm.

Comments:

# Turbine Governor Speed Regulation Test for Electro-Hydraulic Governor

General Information

Unit Code (16 character):   			Location (County) :

Unit Name:  					Date of test:

QSE:						Resource Entity:

Turbine Governor Speed Regulation Test Procedures

- (a)	Simulate unit on line and turbine speed at 3600 RPM.

- (b)	Set load reference at minimum value.

- (c)	Monitor valve demand signal and record as value 'A' (in %).

- (d)	Reduce speed until valve demand just reaches maximum value.
Record valve demand as value 'B' (in %) and speed as value 'C' (in RPM).

- (e)	Set speed at 3600 and load reference at maximum value.

- (f)	Monitor valve demand signal and record as value 'D' (in %).

- (g)	Increase speed until valve demand just reaches minimum value.
Record valve demand as value 'E' (in %) and speed as value 'F' (in RPM).

Turbine Governor Speed Regulation Test Results

|  | A | B | C | D | E | F |
| --- | --- | --- | --- | --- | --- | --- |
| Valve Demand (%) |  |  |  |  |  |  |
| Speed (rpm) |  |  |  |  |  |  |

Speed Regulation With Decreasing Speed

RD=100B−A×3600−C3600×100

Speed Regulation With Increasing Speed

RI=100D−E×F−36003600×100

Comments:

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Rep.:

# Definitions

| System Frequency Response | This response is a function of three key variables; the system's composite governor droop, the percent of spinning capacity which is actually providing governor response, and the frequency response characteristic of the connected load. |
| --- | --- |
| Percent Droop Settings | Also known as Frequency Regulation, Speed Regulation, Speed Sensitivity, Speed Error and others. Percent droop is the percent change in nominal frequency that will cause generator output to change from no load to full load. It is the change in steady state rotor speed, expressed in percent of rated speed, when power output is gradually reduced from rated to zero power. A common percent droop setting is 5% for both high and low frequency excursions. |
| Dead Band | The range of deviations of system frequency (+/-) that produces no turbine governor response, and therefore, no frequency (speed) regulation. It is expressed in percent of rated speed, Hz, or RPM. |
| Valve Position Limiter | A device that acts on the speed and load governing system to prevent the governor-controlled valves from opening beyond a pre-set limit. |
| Blocked Governor Operation | Operating the generating unit with the control system adjusted to prevent the turbine governor from responding to system frequency (speed) variations. In an effort to reduce speed governor operation in some generating units, turbine control systems can be adjusted to block the operation of the governor after the unit is in parallel with the system and is running at its desired output. Selection of a high percent droop characteristic or a large dead band constitutes a form of blocked governor action. |
| Variable Pressure Operation | Varying the boiler pressure to improve turbine efficiency at lower loads. Two methods are normally used. With one method, the turbine governor (G.E.) or control (Westinghouse) valves are positioned in the wide-open position and the generator is changed by changing the boiler pressure. With this method, there is very little, if any response to frequency excursions. With the other method, the valves are positioned at approximately 50% open. The valves are still able to respond to system disturbances. Normal changes in generation requirements are made by varying the boiler pressure until the unit is at rated pressure. After full pressure is reached, the turbine valves are used to make the required generation changes. |

Westinghouse recommends using only this test.

Westinghouse recommends using only this test.