Texas Nodal Market

STATE ESTIMATOR STANDARDS

Version 0.02

August 27, 2007

# Introduction

Nodal Protocol section titled “State Estimator Performance Standard” requires the creation of a State Estimator Performance Standards consistent with the minimum requirements of the Nodal Protocols. This State Estimator Performance Standards document reflects the work of Market Participant and ERCOT technical experts. TAC approves these State Estimator Performance Standards and an appropriate TAC subcommittee is required to update the State Estimator Performance Standards annually each October or more often on a periodic basis as deemed necessary.

ERCOT uses a State Estimator to produce load flow base cases which are used to analyze the reliability of the transmission grid. Accurate and redundant telemetry and an accurate transmission power system model are required by state estimator in order to produce an optimal estimation of the transmission power system state. The state estimator results are used in SCED, contingency analysis, congestion management, and other network analysis real-time sequence functions.

### Acquisition of good telemetry status and analog measurements data (Telemetry) for the transmission power system (System) together with an accurate model of the System are processed by a state estimator to provide an optimal estimate of the System state at a given point in time while filtering measurement noise (error) and detecting gross errors. The quality and availability of telemetry provided to ERCOT are important to the performance of the ERCOT State Estimator.

In case of a conflict between these State Estimator Standards and the Nodal Protocols, the Nodal Protocols shall prevail.

Footnotes in these State Estimator Standards are temporary. They summarize the changes in this version from the previously TAC-approved version.

# Requirements

### State Estimator Performance Requirements

- SE Convergence

State Estimator converges 97% of runs during a monthly test period.

The State Estimator convergence is defined as the following solution parameters:

  - Algebraic sum of MW solved bus mismatch tolerance less than or equal to 15 MW.

  - Algebraic sum of MVAR solved bus mismatch tolerance less than or equal to 15 MVAR.

  - Voltage angle convergence less than or equal to 0.0010 radian.

  - Voltage magnitude convergence less than or equal to 0.0010 per unit.

- Critical Transmission Element Telemetry/SE Accuracy

##### On transmission elements identified as causing 80% of congestion cost in the latest year for which data is available, the difference between the MW telemetry value and the MW SE value shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly.

- Critical Transmission Element SE/Power Flow Accuracy

##### On transmission elements identified as causing 80% of congestion cost in the latest year for which data is available, the difference between the State Estimator results and Power Flow results for critically monitored transmission element MW flows shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly.

- Critical Buss Voltage Accuracy

##### On 20 most voltage critical buses designated by ERCOT and approved by TAC each October; the telemetered bus voltage minus state estimator voltage shall be within the greater of 2% or the accuracy of the telemetered voltage measurement involved for at least 95% of samples measured monthly.

- SCADA Measurement Accuracy

##### On all transmission elements greater than 100kV; the difference between the State Estimator MW solution and the SCADA measurement shall be less than 10 MW or 10% of the associated emergency rating (whichever is greater) on 99.5% of all elements monthly.  All equipment failing this test will be reported to the associated TSP for repair within 10 days of detection.

# MEASURES

To meet objectives of the State Estimator Performance requirements ERCOT will:

##### (1)      ERCOT will work with TSPs and QSEs to resolve problems in accordance with TAC-approved Telemetry Standards prior to directing additional equipment.

##### (2)       In event of failure to meet R2 and R3, ERCOT may direct additional telemetry be installed on elements contributing most to 80% of congestion costs for the latest year for which data is available   If the TSP or QSE disputes the request for additional telemetry the TSP or QSE shall have the appeals process available under the Telemetry Standards.

##### (3)      ERCOT will enforce the requirements of Nodal Protocol “Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows” by alarming any sum of flow around a bus the greater of  5% of the largest line rating connected to the bus or 5MW, and requesting that the applicable TSP or QSE correct the failure.

(4)       ERCOT will post monthly results for compliance with items R1 through R5 above, in accordance with Nodal Protocol Section 8.

- ERCOT shall consider the quality codes sent by the data provider in assigning confidence factors for the data to be used in the State Estimator.  ERCOT’s SCADA equivalent of the ICCP Quality code VALID, with the Current Source equal to the Normal Source, and the Current Provider equal to the Normal Provider shall be considered as good quality.  Quality codes sent with any other quality, Source combination or Provider combination shall be considered at a lower confidence.  The confidence shall continue to decrease over time.  The meaning of the ICCP quality codes and their mapping to ERCOT’s EMS/SCADA system are described in the ERCOT Nodal ICCP Communication Handbook.

##### COMPLIANCE

Compliance to the requirements of these State Estimator Performance Standards shall be governed by the PUCT-approved ERCOT Compliance Process.