## Slide 1: Telemetry and State Estimator Standards
Bill Blevins

## Slide 2: Telemetry Standard proposed changes
Format changed to align with NERC standards format.
Revised intro and removed required Telemetry as this is specified by Protocols
R1 no significant change
R2
  The requirements for TSP telemetry have been separated into their own sections
  Specify the ICCP handbook as source of specific TSP telemetry
  Incorporated prior wording on observability
  Incorporated prior wording on Redundancy
  Specify what criteria is used to obtain new customer owned data

## Slide 3: Telemetry Standard proposed changes
R3
  The requirements for QSE telemetry have been separated into their own sections
R4
  Specify ICCP handbook for SCAN Rates
R5
  Specify ICCP handbook for Data Quality
  Prior standard Quality codes were not correct
R6
  Relocated the existing TSP minimum telemetry criteria from General Performance Criteria to it’s own Requirement
R7
  Relocated the existing Availability requirements from General Performance Criteria to it’s own Requirement
  Revised Availability requirements from 98% of all points achieving 80% availability, to all points achieving 99% availability. The 99% availability is the total availability of all points, not the availability of each point.

## Slide 4: Telemetry Standard proposed changes
R8
  Inserted language to direct actions when ERCOT must locally replace a point for a QSE/TSP
R9
  Revised critically important data
  Added a footnote of the meaning of critical telemetry as any point that leaves the network unobservable if unavailable.
R10
  Modified availability of critical points from 95% of points having 98% availability to all points having 99.9% availability.
R11
  No change
R12
  No change

## Slide 5: Telemetry Standard proposed changes
R13
  ICCP link availability has been changed to 99.9% from 85% to be consistent with the availability requirement for critical data
R14
  Revised the time for a plan for additional telemetry from 18 months to 3 months or provide an alternate plan that will solve the issue within 3 months
R15
  Revised the time for a plan for redundant telemetry from 18 months to 6 months or provide an alternate plan that will solve the issue within 6 months

## Slide 6: State Estimator Proposed Changes
Bill Blevins

## Slide 7: State Estimator Standard proposed changes
Format changed to align with NERC standards format.
R1
  Included SE convergence criteria
R2
  Removed the monthly trial and made the requirement monthly
R3
  Removed the monthly trial and made the requirement monthly
R4
  No Change
R5
  Made the requirement monthly
Measures
  Included QSEs
  Removed reference to section in the old TAC standard and pointed to the Telemetry Standard
  Included reference to Nodal section relating to monthly SE reporting for compliance
  Removed reference to protocol and inserted reference to section title
  Measure 5 referred to the quality codes from the ICCP handbook (Manual is not an ICCP code)
Notes: PUCT Chapter 25 §25.361
Nodal Protocol 3.10.4 ERCOT Responsibilities
Nodal Protocol 3.10.5 TSP Responsibilities
Nodal Protocol 3.10.6 Resource Entity Responsibilities
Nodal Protocol 3.10.7.2 Modeling of Resources and Transmission Loads
Nodal Protocol 3.10.7.5 Telemetry Criteria
Nodal Protocol 3.10.7.5.2 Continuous Telemetry of the Real-Time Measurements of Bus Load, Voltages, Tap Position, and Flows
NERC Reliability Coordination — Facilities
  IRO 002-
    R2, R5,R6,R7
NERC Reliability Coordination — Wide-Area View
  IRO-003
    R2
NERC Reliability Coordination — Current Day Operations
  IRO-003
    R1