## Comments & Responses
State Estimator Standards Comments Version 0.10
Issuing Entity (Name) | Req | ERCOT Suggested Changes | Description | Response Type | Reason / Comment
David J. Bogen (ONCOR) |  | Accurate and redundant telemetry and an accurate transmission power system model are required by state estimator in order to produce an optimal estimation of the transmission power system state. Acquisition of good telemetry status and analog measurements data (Telemetry) for the transmission power system (System) together with an accurate model of the System are processed by a state estimator to provide an optimal estimate of the System system state at a given point in time while filtering measurement noise (error) and detecting gross errors. | Deleted Text (optimal ) Deleted Text (System ) Inserted Text (system ) | Accepted
David J. Bogen (ONCOR) | R1. SE Convergence | State Estimator converges 97% of runs during a monthly test period. | Deleted Text (test ) | Accepted
Valentine Emesih (CNP) | R1. SE Convergence | SE Convergence | 97% may need further qualification: There are several reasons why SE may not run every 5 minutes and converge 97% of the time: telemetry issues, communication issues, seasonal applicaion tunning, modelling issues, daily database builds etc.
David J. Bogen (ONCOR) | R2. Critical Transmission Element Telemetry/SE Accuracy | For “Critically Important Telemetry” as define in the Texas Nodal Market Telemetry Standard, the difference between the MW telemetry value and the MW SE value shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly. On transmission elements identified as causing 80% of congestion cost in the latest year for which data is available, the difference between State Estimator results and Power Flow results for critically monitored transmission element MW flows shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly. | Inserted Text (For “Critically Important Telemetry” as define in the Texas Nodal Market Telemetry Standard, the difference between the MW telemetry value and the MW SE value shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly.) Deleted Text (On transmission elements identified as causing 80% of congestion cost in the latest year for which data is available, the difference between State Estimator results and Power Flow results for critically monitored transmission element MW flows shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly)
David J. Bogen (ONCOR) | R3. Critical Transmission Element SE/Power Flow Accuracy | For “Critically Important Telemetry” as define in the Texas Nodal Market Telemetry Standard, the difference between State Estimator results and Power Flow results for critically monitored transmission element MW flows shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly On transmission elements identified as causing 80% of congestion cost in the latest year for which data is available, the difference between the MW telemetry value and the MW SE value shall be less than 3% of the associated element emergency rating on at least 95% of samples measured in a one month trial. | Inserted Text (For “Critically Important Telemetry” as define in the Texas Nodal Market Telemetry Standard, the difference between State Estimator results and Power Flow results for critically monitored transmission element MW flows shall be less than 3% of the associated element emergency rating on at least 95% of samples measured monthly ) Deleted Text (On transmission elements identified as causing 80% of congestion cost in the latest year for which data is available, the difference between the MW telemetry value and the MW SE value shall be less than 3% of the associated element emergency rating on at least 95% of samples measured in a one month trial) | Accepted
David J. Bogen (ONCOR) | R4. Critical Buss Voltage Accuracy | On the 20 most voltage critical buses designated by ERCOT and approved by TAC each October | Corrected typo
Valentine Emesih (CNP) | R2,R3,R4,R5 |  | ERCOT has enough data today to verify that this is a reasonable requirment. A potential device that is 5% accurate, monitored by a 3% meter may not be in the threshold of accuracy required.
Dennis Kunkel (AEP) | R5. Scada Measurement Accuracy | "All equipment failing this test will be reported to the associated TSP for repair within 10 days of detection." | "All equipment failing this test will be reported to the associated TSP for repair within 10 days of detection." My understanding is that this is a requirement on ERCOT to report to the TSP within 10 days of ERCOT detecting a problem, not that the TSP has 10 days to repair. If it is 10 days to repair, then it should state 10 business days and should be defined from the date of ERCOT reporting this in writing to the TSP.
Jim Pape (Luminant) | R5. SCADA Measurement Accuracy | All equipment failing this test will be reported to the associated TSP for repair within 10 days of detection. | Deleted Text ( within 10 days of detection)
David J. Bogen (ONCOR) | R5. SCADA Measurement Accuracy | All equipment failing this test will be reported to the associated TSP for repair within 10 days of detection. | Deleted Text ( within 10 days of detection)
David J. Bogen (ONCOR) | C. MEASURES | (3) ERCOT will enforce the requirements of Nodal Protocol 3.10.7.45.2 (5) by alarming any sum | corrected protocol reference

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.