## Comments & Responses
Telemetry Standards Comments Version 0.10
Issuing Entity (Name) | Req | ERCOT Suggested Changes | Description | Response Type | Reason / Comment
Dennis Kunkel (AEP) | General comments |  | There are several general concerns. The main one is that it states we must have telemetry availability to ERCOT 99% of the time during each month. This means we can only have a 1% error rate. Is this reasonable?
Dennis Kunkel (AEP) | General comments |  | We have approximately 490 RTU's , this mean we can only have 4 RTU's down at any given time. At this moment we have 5 down, in Texas.
Dennis Kunkel (AEP) | General comments |  | What about a failed microwave tower that may have 5 or 6 RTU's on it. Say it takes 2 hours to get to the location to just trouble shoot it. Which could be the case in Texas. We're in violation in just one case.
Dennis Kunkel (AEP) | General comments |  | What about the phone company digging through the communications line. This has happened several times, and with it half or all of our communications go down for hours.
Dennis Kunkel (AEP) | General comments |  | The document states it will exclude "approved planned outages". Does this mean everything we do will have to be reported to ERCOT? Field personnel are working on several RTU's a day for repairs/upgrades/maintenance. In so doing, they will power down and power back up the RTU. Does this mean that every time someone does anything with an RTU they're going to have to call ERCOT and get approval to do their work?
Dennis Kunkel (AEP) | General comments |  | For the SCADA department, the most frequent reason for availability to be lost would be when we are putting on a new data base. There is so much work going on, in particular RTU work, that the SCADA department puts on a new database almost daily. Sometimes more than once a day. When we put on a data base, communications are stopped then restarted. This means we loose all communications to all the RTU's then they re-link up. To be on the safe side, lets say it takes a minute to get all the RTU's back up scanning. If we do this once a day, which is typical, then we are down approximately 30 minutes a month. Are we going to have to call and get approval to do our work every day, which most of the time our work is to make sure we are gathering accurate data and supplying it accurately.
Dennis Kunkel (AEP) | General comments |  | I'm sure there are many more reasons for communications to fail, so I'm questioning if 1% error is reasonable. And if it is reasonable for ERCOT to expect us to call them when we are trying to do our jobs.
Dennis Kunkel (AEP) | General comments |  | Lastly, what if the communications failure is on ERCOT's end. The document isn't specific on ERCOT's responsibilities for failures.
Dave Sutherland (LCRA) | General comments |  | In summary, we believe there should be more discussion associated with the significant changes proposed. NDSWG should play a significant role in developing the Telemetry Standards.
David J. Bogen (ONCOR) | Introduction | ERCOT is charged by the Nodal Protocol 3.10.7.4 to create Telemetry CriteriaTAC is charged by the Nodal Protocols, 3.10.7.5(1) to establish a task force that is open to Market Participants, comprised of technical experts to develop a set of Telemetry Criteria consistent with the minimum requirements of the Protocols.
David J. Bogen (ONCOR) | Introduction | TAC approves the Telemetry Standards Criteria and an appropriate TAC subcommittee is required to shall update the Telemetry Standards annually each October or more often on a periodic basis as deemed necessary.
David J. Bogen (ONCOR) | Introduction | As directed by the Nodal Protocols, these Telemetry Standards are to support the State Estimator in meeting the approved performance standard, and to support TAC-approved accuracy standards for the calculation of LMPs.designed to ensure proper performance of the aforementioned applications.
Eric Woelfel (Formosa) | R1 Telemetry of Breaker and Switch Status |  | I find this paragraph confusing about what breakers will be required to have telemetry. We have our own private network, with breakers and switch gear on 138
David J. Bogen (ONCOR) | R1 Telemetry of Breaker and Switch Status | R1. Telemetry of Breaker and Switch Status [NP: 3.10.7.45.1(1))] | correct protocol reference | Accepted
Valentine Emesih (CNP) | R2. Required TSP Telemetry | Protocol Reference | Change to 3.10.7.5 | Accepted
David J. Bogen (ONCOR) | R2. Required TSP Telemetry | R2. Required TSP Telemetry [NP: 3.10.7.45.2(3)] Each TSP shall provide telemetered measurements on modeled Transmission Elements to ensure State Estimator observability of any monitored voltage and power flow between their associated transmission breakers needed to the extent such can be shown to be needed in achieving the TAC-approved State Estimator performance standard. ........ ERCOT may request additional measurements where “N-1 Redundancy” does not exist. In making the determination to request additional telemetry, ERCOT shall consider the economic implications of inaccurate representation of Load Models in LMP results versus the cost to remedy. .............. TSP’s shall obtain the required data from retail customers associated with new customer-owned substations as defined by requirements R14 and R15. If the data cannot be obtained, ERCOT shall report such cases to the Independent Market Monitor. This should not be construed to indicate that all retail customers owned substations would be required to provide telemetry.
Valentine Emesih (CNP) | R2. Required TSP Telemetry | On monitored substations, each TSP shall install, at the direction of ERCOT, sufficient telemetry such that there is an “N-1 Redundancy.” | Statement should read (per protocol - See 3.10.7.5(3): "On monitored, Non-load, substations, each TSP shall install, at the direction of ERCOT, sufficient telemetry such that there is an “N-1 Redundancy.”
Valentine Emesih (CNP) | R2. Required TSP Telemetry | TSP’s shall obtain the required data from retail customers associated with new customer-owned substations as defined by requirements R14 and R15. If the data cannot be obtained, ERCOT shall report such cases to the Independent Market Monitor. | ERCOT should send these requests directly to the private facility owners. This issues was previously addressed.
Eric Woelfel (Formosa) | R3 Required QSE Telemetry |  | Could you specify the section and tables in the ICCP Handbook that are applicable? There are many tables in this section.
Dennis Kunkel (AEP) | R4. Telemetry Scan Rates |  | "In no case shall field telemetered data be delayed beyond the specified scan rates due to a point's propagation through one or more intermediate systems." I don't really know if my concern applies here, but when there has been a lot of activity, we have had SCADA time stamps drift up to 8 seconds when compared to actual IRIG stamps; this may be due to channel loading issues, maybe not.
Eric Woelfel (Formosa) | R4. Telemetry Scan Rates |  | Could you specify the section and tables in the ICCP Handbook that are applicable? For instance, Table 27.
Jim Pape (Luminant) | R4. Telemetry Scan Rates | Data acquired through field telemetry shall be made available to ERCOT through the configuration set forth in the Handbook. least number of intermediate systems possible. In no case shall field telemetered data be delayed beyond the specified scan rates due to a point’s propagation through one or more intermediate systems. | Inserted Text ( configuration set forth in the Handbook. ) Deleted Text (least number of intermediate systems possible. In no case shall field telemetered data be delayed beyond the specified scan rates due to a point’s propagation through one or more intermediate systems.)
Jim Pape (Luminant) | R4. Telemetry Scan Rates | NOTE: R4 changes are subject to interpretation and generally do not set a proper standard. “Least number of systems possible” is not the same thing as least number of systems practical or cost effective. None of these are proper standards. “In no case shall field telemetered data be delayed beyond the specified scan rates due to a point’s propagation through one or more intermediate systems.” Read literally from one point of view, the RTU points would have to be provided to ERCOT within 2 seconds which is not possible unless ERCOT reads the RTU directly. From another interpretation, it says it takes as long as it takes to propagate through the systems which is meaningless for a standard. | Inserted Text
David J. Bogen (ONCOR) | R4. Telemetry Scan Rates | The data exchange tables in that document specify the frequency of scan rates to be used within ERCOT to the extent as supported by the Nodal Protocols. Data acquired through field telemetry shall be made available to ERCOT through the least number of intermediate systems possible. In no case shall field telemetered data be delayed beyond the specified scan rates due to a point’s propagation through one or more intermediate systems.
Eric Woelfel (Formosa) | R5 Data Quality |  | Could you specify the section for quality codes in the ICCP Handbook? For example: 4.5.2 Resource Status Codes
Valentine Emesih (CNP) | R5 Data Quality | Market Participant’s shall provide documentation to ERCOT describing their native system quality codes and defining the conversion of their quality codes into the ERCOT defined ICCP quality codes consistent with the ERCOT Nodal ICCP Communication Handbook. | What is the intent of providing this documentation and how does ERCOT intend to use? Are there issues with QC interpretation in the ICCP handbook. PtP test was intended to verify that the QC match ICCP handbook format.
Valentine Emesih (CNP) | R6. Minimum Telemetry Criteria | busmeasurements around each substation Buss such that they are less than the greater of 5 MW or 5% of the largest normal line rating at each bus.or 5 MW, whichever is greater. | A an observable telemetered bus may not have enough telemetry to perform this check. The language should be changed to remove "Each substation Bus"
David J. Bogen (ONCOR) | R6. Minimum Telemetry Criteria | R6. Minimum Telemetry Criteria [NP: 3.10.7.45.2(5)] …...each Electrical Bus substation Buss such that they are less than 5% of the
Dennis Kunkel (AEP) | R7. Telemetry Availability |  | "All points made available to ERCOT must achieve a monthly availability of 99%." What is the basis for tightening up this from "98% of all points achieving 80% availabiltiy"? 1% downtime or bad data is going to be almost impossible to achieve. How will we achieve 99%, when we have to maintain and repair equipment by taking it out of scan or by introducing test data? I don't see where the allowance for removing maintenance time, etc. from the availability calculation is being made. 1% is only 3.5 days per year, and 1% is 7 hours per month. You cannot respond to something and fix it that fast.
Valentine Emesih (CNP) | R7. Telemetry Availability | Ninety eight (98%) percent of all telemetry provided to ERCOTAll points made available to ERCOT by each QSE or TSP must achieve a quarterlymonthly availability of eighty (80%)99% percent or better. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with good quality codes at the scheduled periodicity. | This change should be rejected because the new requirement is unreasonable. There is no valid reason to change existing standard. 1% of the total number of seconds in a 30 day month is about 26000 seconds. For a TSP that exchanges 7000 points, average allowed outage per point is less than 4 seconds per point per month. On an ICCP link reset (either from ERCOT or MP) all data points will be stale for as nuch as a full minute. With a 5 minute State Estimation cycle time this “violation” - a 4 sec. data loss - is insignificant. Moreover, the new requirement ( as stated above) is more stringent for MP that send large sets of data, and totally ignore the operating realities of a SCADA and associated communication system.
Dave Sutherland (LCRA) | R7. Telemetry Availability |  | Requirement R7 went from 98% of the points required to have an availability of 80% quarterly, to 100% of the points required to have an availability of 99% monthly. We believe that this requirement is not practical or achievable by any of the market participants.
Dave Sutherland (LCRA) | R7. Telemetry Availability |  | Requirement R7 formula appears to be incorrect. It would be more accurate to calculate the average availability of all points. To make this an average the “n” in the formula needs to be all points that are being received by ERCOT and not just the points that are not VALID. Also n needs to be applied as a multiplier to “T” in the formula.
Jim Pape (Luminant) | R7. Telemetry Availability | All points made available to ERCOT by each QSE or TSP must achieve a quarterlymonthly availability of eighty 99% 93% percent or better and a quarterly availability of 95% or better.
David J. Bogen (ONCOR) | R7. Telemetry Availability | ……...Real-Time data with good valid quality codes at the scheduled periodicity. Telemetry points that are reported as being unavailable shall not be included in this analysis for the time frame that has been scheduled.
Dennis Kunkel (AEP) | R8. Locally and Remotely Replaced Telemetry |  | don't understand the requirement of "TSP shall fix those remotely replaced telemetry within 1 day". If something is broken, you may not be able to fix it in one day. What is this really referring to?
Valentine Emesih (CNP) | R8. Locally and Remotely Replaced Telemetry | Telemetry remotely replaced by TSP or QSE will be reported to the responsible entity. TSP and QSE shall fix those remotely replaced telemetry within 1 day. | Again this is unreasonable. I assume turn around time for field instruments may exceed 1 day. Moreover, this is neither consistent with R7 nor R11. It is difficult to understand the rationale for this change
Jim Pape (Luminant) | R8. Locally and Remotely Replaced Telemetry | Telemetry remotely replaced by TSP or QSE will be reported to the responsible entity. TSP and QSE shall fix those remotely replaced telemetry within 1 day. | Deleted Text (TSP and QSE shall fix those remotely replaced telemetry within 1 day.)
Dennis Kunkel (AEP) | R9. Availability of Critically Important Telemetry |  | With this level of availability, I would think a State Estimator would be unnecessary. This is unattainable in my opinion. Why was this changed from "95% of points having 98% availability"?
Eric Woelfel (Formosa) | R9. Availability of Critically Important Telemetry |  | How are these 20 points to be defined? Also why only 20 points? What is the basis for this? This requirement seams too vague.
Dave Sutherland (LCRA) | R9. Availability of Critically Important Telemetry |  | Requirement R9, the definition of critical telemetry, went from being very specific to being very vague.
David J. Bogen (ONCOR) | R9. Availability of Critically Important Telemetry | ERCOT will identify critical measurements, not to exceed 10% of the Transmission Elements in ERCOT, and 20 voltage points……. .........ERCOT will review and publish this list annually. ERCOT will use the following criterion to identify critically important Telemetry: (1) Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above. (2) Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer. (3) Loss of a telemetry point that results in the inability of ERCOT to monitor the loading on transmission facilities designated as critically important to transmission reliability by ERCOT. A list of critical facilities will be published annually. (4) Telemetry necessary to monitor transmission elements identified as causing 80% of congestion cost in the year for which the most recent data is available
Eric Woelfel (Formosa) | R10 Availability for Critical Import Telemetry |  | This paragraph is incomplete and missing a sentence on the requirements.
Jim Pape (Luminant) | R10 Availability for Critical Import Telemetry | percent or better. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with VALID ICCP quality codes at the scheduled periodicity.
Jim Pape (Luminant) | R10 Availability for Critical Import Telemetry | All critical points made available to ERCOT by each QSE or TSP must achieve a monthly availability of 99.997% percent or better. | Deleted Text (99.9) Inserted Text (97)
Dave Sutherland (LCRA) | R10 Availability for Critical Import Telemetry |  | Requirement R10 went from 95% of the critical points requiring a quarterly 90% availability to a 100% of critical points requiring monthly availability of 99.9%. We believe that this new proposed requirement is not practical or realistic.
Valentine Emesih (CNP) | R10 Availability for Critical Import Telemetry | Each QSE or TDSP shall provide data to ERCOT that meets the following availability:Ninety five (95%) percent of the critically important telemetry defined by ERCOT must achieve a quarterly availability of ninety (90%)QSE or TSP must achieve a monthly availability of 99.9% percent or better. | This change should be rejected because the new requirement is unreasonable. There is no valid reason to change existing standard.
David J. Bogen (ONCOR) | R10 Availability for Critical Import Telemetry | percent or better. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with VALID ICCP quality codes at the scheduled periodicity. All 95% of the critical points made available to ERCOT by each QSE or TSP must achieve a monthly quarterly availability of 99.990% percent or better. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with VALID ICCP quality codes at the scheduled periodicity. Any telemetered point that has a reported as outaged shall be removed from this calculation.
Valentine Emesih (CNP) | R11. Restoration of Failed Telemetry and repair of inaccurate telemetry |  | Misbehaving equipment should be changed to "Faulty Equiment" in bullet item (1)
David J. Bogen (ONCOR) | R11. Restoration of Failed Telemetry and repair of inaccurate telemetry | Telemetered data shall be provided continuously at the scan rates specified hereinby the ERCOT Nodal ICCP Communication Handbook or the Nodal Protocols. When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, either
Valentine Emesih (CNP) | R12 Calibration, Quality Checking and Testing | It is the responsibility of the owner either TSP or QSE to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis, and that accuracy meets or exceeds that which is specified in this Appendix consistent with Good Utility Practice, for both the overall system and for individual equipment where detailed herein. . | This is a good. "Consistent with Good Utility Practice" should be sprinkled all over this document.
Jim Pape (Luminant) | R12 Calibration, Quality Checking and Testing | It is the responsibility of the owner either TSP or QSE to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis consistent with Good Utility Practice, for both the overall system and for individual equipment. | Deleted Text (either TSP or QSE )
Jim Pape (Luminant) | R12 Calibration, Quality Checking and Testing | Coordination of outages required for these activities with ERCOT is also the responsibility of the owner. Each TSP/QSE shall have a plan on file with ERCOT to assure accurate telemetry of data. If an owner TSP/QSE repeatedly fails other telemetry metrics defined in these Telemetry Standards, ERCOT may require a revision of the plan. | Deleted Text (Each TSP/QSE shall have a plan on file with ERCOT to assure accurate telemetry of data.) Inserted Text (n owner) Deleted Text (TSP/QSE )
Valentine Emesih (CNP) | R13. Reliability of ICCP Links | For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT’s control centers with updates of all data continuing at a 30 second or less scan rate. at a 30 second or less. | This may need rewording
Valentine Emesih (CNP) | R13. Reliability of ICCP Links | ICCP links must achieve a monthly availability of 99.9% percent, excluding approved planned outages. | What is the rational for changing the previous description? Does ERCOT outage information validate this to be a more practical requirment?
Dave Sutherland (LCRA) | R13. Reliability of ICCP Links |  | Requirement R14 for implementation of additional telemetry as requested by ERCOT has been reduced from 18 months to 3 months. We believe that this change is onerous and will be difficult to meet.
Jim Pape (Luminant) | R13. Reliability of ICCP Links | ICCP links must achieve a monthly availability of ninety-nine point seven nine (99.79%) percent, excluding approved planned outages. | Inserted Text (7) Deleted Text (9) Deleted Text (approved )
David J. Bogen (ONCOR) | R13. Reliability of ICCP Links | R13. Reliability of ICCP Links [NP: 3.10.7.45(4)] Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data. This will include establishing a process to coordinate downtime for ICCP links and database maintenance.The nodal Operating Guide Section 7, defines the methodology that will be used in this analysis.
Dennis Kunkel (AEP) | R14. Requests for Additional Telemetry |  | "...within 3 months..." Why was this changed from 18 months to 3 months? Recommend we stay with previous time of 18 months. Equipment and design may not be available to provide this within 3 months.
Valentine Emesih (CNP) | R14. Requests for Additional Telemetry | Request for additional telemetry changed from 18 months to 3 months. | Reject all changes. There is no credible basis for the suggested changes. Engineering, procurment, and construction will generally take at 12-18 months.
Jim Pape (Luminant) | R14. Requests for Additional Telemetry | (1) Accept ERCOT’s request for additional telemetry, provide the telemetry within 3 9 months and notify ERCOT of the implementation schedule; (2) Provide an alternative proposal to ERCOT, for implementation within the next 3 9 months, which meets the requirements described by ERCOT; | Deleted Text (3 ) Inserted Text (9)
David J. Bogen (ONCOR) | R14. Requests for Additional Telemetry | When ERCOT identifies a reliability concern, a deficiency in system observability, or a deficiency in measurements to support the representation of Model Loads, and that concern or deficiency is not due to any inadequacy of the State Estimator program, ERCOT may request that a TSP or QSE provide additional telemetry measurements. ERCOT may request additional telemetry when it determines that network observability or the measurement redundancy is not adequate to produce acceptable state estimator results.
Dennis Kunkel (AEP) | R15. Request for Redundant Telemetry |  | "...within 6 months..." Why was this changed from 18 months to 6 months? Recommend we stay with previous time of 18 months. Equipment and design may not be available to provide this within 6 months.
Valentine Emesih (CNP) | R15. Request for Redundant Telemetry | Request for Redundant telemetry changed from 18 months to 6 months. | Reject all changes. There is no credible basis for the suggested changes. Engineering, procurment, and construction will generally take at 12-18 months.
Dave Sutherland (LCRA) | R15. Request for Redundant Telemetry |  | Requirement R15 for implementation of redundant telemetry as requested by ERCOT has been reduced from 18 months to 6 months. We believe that this change is also onerous and will be difficult to meet.
Valentine Emesih (CNP) | R15. Request for Redundant Telemetry | Indicate that the requested telemetry point is at a location where the TDSPTSP or QSE does not have the authority to install the requested telemetry. For points on privately owned facilities connected to the ERCOT Transmission Grid, an attempt will be made to facilitate ERCOT's telemetry request; | ERCOT should directly send these requests directly to the private facility asset owners
Jim Pape (Luminant) | R15. Request for Redundant Telemetry | Upon receipt of a request for redundant telemetry, a TSP or QSE has sixty (60) days to: | Deleted Text (approved )
Jim Pape (Luminant) | R15. Request for Redundant Telemetry | Provide ERCOT with a schedule of equipment installations within nine the next six (69) months which will provide the proposed telemetry; (2) Propose an alternative solution which will serve the same purpose as the ERCOT identified telemetry additions with a proposed implementation within 6 9 months; | Inserted Text ( nine) Deleted Text (the next six ) Deleted Text (6 ) Inserted Text (9 )

## Punch List
Document Name:
Punch List # | Punch List Description | Related TPTF Comment

## Data Entry Lists
Response | Description
Accepted | Comment accepted and requirements document updated as per the comment.
Clarification Provided* | Clarification provided and requirements document updated to clarify
Clarification Provided | Clarification provided and no updates made to the requirements document.
Pending | Issue is not resolved yet. All pending issues will be dispositioned to a punch list and resolved later. These issues need more time and coordination across multiple Nodal projects.
Rejected | Comment rejected as it does not comply with Nodal Protocols.