DRAFT COPY FOR REVIEW USE ONLY

Includes Comments from 9/17 ROS/Telemetry Standards Workshop

Texas Nodal Market

Telemetry Standards

Version 0.06

August 27, 2007

# Introduction

ERCOT TAC is charged by the Nodal Protocol 3.10.7.5 to create Telemetry Criteria. This Telemetry Standards document specifies the Telemetry Criteria called for in the Nodal Protocols.  TAC approves the Telemetry Standards and an appropriate TAC subcommittee is required to update the Telemetry Standards annually each October or more often on a periodic basis as deemed necessary.

Acquisition of good status and analog measurements of the transmission power system together with an accurate power system model of the system are processed by a State Estimator to provide an optimal estimate of the power system state at a given point in time while filtering measurement noise  and detecting gross errors. The quality and availability of telemetry provided to ERCOT are important to the performance of the ERCOT State Estimator and the LMP calculations. As directed by the Nodal Protocols, these Telemetry Standards are designed to ensure proper performance of the aforementioned applications.

In case of a conflict between these Telemetry Standards and the Nodal Protocols, the Nodal Protocols shall prevail.

Footnotes in these Telemetry Standards are temporary. They summarize the changes in this version from the previously TAC-approved version.

- Requirements

## Operations Requirements

- Telemetry of Breaker and Switch Status [NP: 3.10.7.5.1(1))]

Each TSP and QSE shall provide telemetry, to ERCOT on the status of all breakers and switches used to switch any Transmission Element or load modeled by ERCOT.  Each TSP and QSE is not required to install telemetry on individual breakers and switches, where the telemetered status shown to ERCOT is current and free from ambiguous changes in state caused by the TSP or QSE switching operations and TSP or QSE personnel.  Each TSP or QSE shall update the status of any breaker or switch through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute.  If in the sole opinion of ERCOT, the manual updates of the TSP or QSE have been unsuccessful in maintaining the accuracy required to support State Estimator performance to the State Estimator Performance Standard, ERCOT may request that the TSP or QSE install complete telemetry from the breaker or switch to the TSP or QSE, and then to ERCOT.  If the TSP disputes the request for additional telemetry the TSP shall have the appeals process available under R14 or R15 as applicable. In making the determination to request installation of additional telemetry from a breaker or switch, ERCOT shall consider the economic implications of inaccurate representation of Model Loads in LMP results versus the cost to remedy.

- Required TSP Telemetry [NP: 3.10.7.5.2(3)]

Each TSP shall provide telemetered measurements on modeled Transmission Elements to ensure State Estimator observability of any monitored voltage and power flow between their associated transmission breakers needed in achieving the TAC-approved State Estimator performance standard. On monitored non-Load substations, each TSP shall install, at the direction of ERCOT, sufficient telemetry such that there is an “N-1 Redundancy.”  An N-1 Redundancy exists if the flow remains observable on the loss of any single measurement pair (MW, MVAR) excluding station communication path failures.

- TSPs are required to provide power operation data to ERCOT as defined in the ERCOT Nodal ICCP Communication Handbook. ERCOT will monitor the validity of the Network Model as it affects State Estimator results in order to determine additional required data.

Non-TSP substation owners shall provide the required data to their interconnected TSP as defined by requirements R14 and R15.  If the data cannot be obtained, ERCOT shall report such cases to the Independent Market Monitor.

- Required QSE Telemetry [NP: 6.5.5.2(2)]Error: Reference source not found

QSEs are required to provide power operation data to ERCOT as defined in the ERCOT Nodal ICCP Communication Handbook. The data exchange tables in that document represent all potential data required.

- Telemetry Scan Rates [NP: 3.10.7.5(3)]

ERCOT will scan QSE and TSP data at scan rates as defined in the ERCOT Nodal ICCP Communication Handbook. The data exchange tables in that document specify the frequency of scan rates to be used within ERCOT. Data acquired through field telemetry shall be made available to ERCOT through the least number of intermediate systems possible. In no case shall field telemetered data be delayed beyond the specified scan rates due to a point’s propagation through one or more intermediate systems.

- Data Quality

Market Participant’s shall provide documentation to ERCOT describing their native system quality codes and defining the conversion of their quality codes into the ERCOT defined ICCP quality codes consistent with the ERCOT Nodal ICCP Communication Handbook.

## Maintenance Requirements

- Minimum Telemetry Criteria [NP: 3.10.7.5.2(5)]

The TSP or QSE shall maintain the algebraic sum of the telemetered measurements around each Electrical Buss such that they are less than 5% of the largest normal line rating or 5 MW, whichever is greater.

- Telemetry Availability

All points made available to ERCOT must achieve a monthly availability of ninety nine (99%) percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with VALID quality codes at the scheduled periodicity.

Where:

A =	percent availability of all points received from a given QSE or TSP.

T =	total number of seconds in the month.

i =	the ith point having a quality code other than VALID

n =	total number of points having a quality code other than VALID

Bi =	number of seconds during the month that the ith point had quality other than VALID.

- Locally and Remotely Replaced Telemetry

In the event that ERCOT identifies a telemetered value which it believes is incorrect, it shall notify the providing entity, and direct them to manually replace the erroneous data until the error is corrected.

ERCOT shall not manually replace telemetry status or analogs from TSP’s or QSE’s unless the TSP or QSE notifies them that they are technically incapable of performing a manual replace function due to technical difficulties at their facility.  In this event, ERCOT shall notify market participants thru the Event Notification System (ENS) until the technical difficulty is resolved.

Telemetry remotely replaced by TSP or QSE will be reported to the responsible entity.  TSP and QSE shall fix those remotely replaced telemetry within 1 day.

- Critically Important Telemetry

ERCOT will identify critical measurements and 20 voltage points that are “critically important” to reliability, system observability, support of State Estimator performance, or the commercial Market. This telemetry will be considered “Critically Important Telemetry” in the context of this document.

- Availability for Critically Important Telemetry

All critical points made available to ERCOT by each QSE or TSP must achieve a monthly availability of 99.9% percent or better. Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with VALID ICCP quality codes at the scheduled periodicity.

- Restoration of Failed Telemetry and repair of inaccurate telemetry

Telemetered data shall be provided continuously at the scan rates specified herein.  Lost data or signals, whether failed or in error, must be restored promptly by the provider of the telemetered data.  It is recognized that some data may be more critical than other data.  ERCOT will inform the TSP or QSE if a data item is critical and needs to be repaired as quickly as possible.  QSE and TSP repair procedures and records shall be made available to ERCOT upon request.

Before ERCOT requests review/re-calibration of a problem piece of equipment it shall discuss the problem with the provider to attempt to arrive at a consensus decision on the most appropriate action.

When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, either

When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, either

- Calibrate/repair the malfunctioning equipment

- Request an outage to schedule calibration/repair of the malfunctioning equipment

- Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame or

- Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.

- Calibration, Quality Checking and Testing

It is the responsibility of the owner either TSP or QSE to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis consistent with Good Utility Practice, for both the overall system and for individual equipment.

Coordination of outages required for these activities with ERCOT is also the responsibility of the owner.  Each TSP/QSE shall have a plan on file with ERCOT to assure accurate telemetry of data.   If a TSP/QSE repeatedly fails other telemetry metrics defined in these Telemetry Standards, ERCOT may require a revision of the plan.

- Reliability of ICCP links  [NP:3.10.7.5(4)]

Each TSP and QSE shall use fully redundant data communication links (between its control center systems and ERCOT systems such that any single element of the communication system can fail and:

- For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and

- For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT with updates of all data continuing at a 30 second or less scan rate.

ICCP links must achieve a monthly availability of ninety-nine point nine (99.9%) percent, excluding approved planned outages.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data.  This will include establishing a process to coordinate downtime for ICCP links and database maintenance.

## New Construction

### Requests for Additional Telemetry [3.10.7.5(6)]

ERCOT is required to monitor transmission assets operated at 60 kV or above.  To do this, ERCOT may request that additional MW, MVAR, and voltage telemetry be installed, while attempting to minimize adding equipment to as few locations as practicable.

ERCOT may request additional telemetry when it determines that network observability or the measurement redundancy is not adequate to produce acceptable state estimator results.

Prior to making a request for additional telemetry, ERCOT will provide evidence supporting a congestion or reliability problem requiring additional observability and define expected improvements in system observablity needed.  If the request is for telemetry additions at more than one location, ERCOT will prioritize the requested additions.

Upon receipt of a request for additional telemetry, the TSP or QSE will have sixty (60) days to either:

(1)	Accept ERCOT’s request for additional telemetry and provide a schedule for its implementation within 3 months.

(2)	Provide an alternative proposal to ERCOT, for implementation within the next 3 months, which meets the requirements described by ERCOT;

(3)	Propose a normal topology change (change normal status of switch (es)) in the area which would eliminate the security violations which are ERCOT’s concern. (i.e. eliminates the possibility of flow through a networked element and turns the security problem into a planning problem which is un-affected by unit dispatch);

(4)	If ERCOT rejects the alternate solution, the TSP or QSE may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.

(5)	Indicate that the requested telemetry point is at a location where the TSP or QSE does not have the authority to install the requested telemetry.  For points on privately owned facilities connected to the ERCOT Transmission Grid, an attempt will be made to facilitate ERCOT's telemetry request; or

(6)	File a request with the PUCT requesting expedited action for an Order directing that the responsibility for reliability and protection of this specific element or elements of the transmission system be withdrawn from ERCOT and assigned to the requesting TSP.  ERCOT will then immediately remove the elements from its Real Time Congestion Management system as monitored elements pending the PUCT decision.

If ERCOT has not received acknowledgement that a request has been received within thirty (30) days of its sending, ERCOT will contact the TSP or QSE for verification of receipt.

- Requests for Redundant Telemetry

ERCOT will maintain redundancy on measurements critical to transmission reliability of the ERCOT interconnection.  ERCOT will identify and produce a list of telemetry points in the ERCOT system that is critical to the state estimator solution.  This list will be published annually.  ERCOT will use this list to identify telemetry points whose loss will result in:

(1)	Inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(2)	Inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(3)	Inability of ERCOT to monitor loading on transmission facilities designated as critical to transmission reliability by ERCOT. A list of critical facilities will be published annually.

ERCOT may request additional MW, MVAR and voltage telemetry to make these measurements redundant.  In this request, ERCOT will identify the critical points, and the contingency/overload condition and the unit dispatch which makes this a possible concern. If the request is for telemetry at multiple locations, ERCOT will prioritize the requested additions.

Upon receipt of a request for redundant telemetry, a TSP or QSE has sixty (60) days to:

(1)	Provide ERCOT with a schedule of equipment installations within the next six (6) months which will provide the proposed telemetry;

(2)	Propose an alternative solution which will serve the same purpose as the ERCOT identified telemetry additions with a proposed implementation within 6 months;

(3)	In cases where the request is based on the availability rate of an existing telemetry point, the TSP or QSE will provide a plan to improve the availability rate of the identified critical telemetry to an acceptable level, or provide documentation for why this cannot be accomplished;

(4)	If ERCOT rejects the alternate solution, the TSP or QSE may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.

(5)	Identify and propose a schedule of equipment installations within the next 18 months which would, as a result, make the transmission element identified by ERCOT non-critical; or

(6)	Indicate that the facility that telemetry is being requested is not owned or covered by an interconnect agreement that allows the requested party to install the additional telemetry.

If ERCOT does not have knowledge that a request has been received within thirty (30) days of its sending, ERCOT will contact the TSP or QSE for verification of receipt.

# Compliance

Compliance to the requirements o these Telemetry Standards shall be governed by the PUCT-approved ERCOT compliance Process.

The requirements for TSP and QSE telemetry have been separated into their own sections. Data exchange requirement are now in the ICCP Handbook rather than being listed in the Telemetry Standards.

Scan rate requirements have been changed to reflect the actual data exchange requirements of the market.

The Data Quality provision of the previous version of the Telemetry Standards addressed quality codes directly. Data quality is extensively treated in the ICCP Handbook, so this version of the Telemetry Standards refers to the ICCP Handbook.

Availability requires have been changed from 98% of all points achieving 80% availability, to all points achieving 99% availability. The 99% availability is the total availability of all points, not the availability of each point.

This requirement the number of voltage points to approximately 20... The previous version of the standard limited the number of voltage point to no more than 20.

A critical measurement is a measurement which will leave a portion of the transmission network un-observable if unavailable.

Availability of critical points has been changed from 95% of points having 98% availability to all points having 99.9% availability. The 99.9% availability is the total availability of all critical points, not the availability of each point

ICCP link availability has been changed to 99.9% from 85% to be consistent with the availability requirement for critical data.