Texas Nodal:

EDS LFC Testing

MP Handbook – DRAFT

This is a living document.  The document and its contents have been drafted for discussion during the EDS LFC Market Participant Workshop. Based on the Workshop, ongoing planning meetings, and Nodal Project deliveries the details will be further refined.

Version 0.03

Wednesday, September 12th, 2007

Revision History

| Document Revisions |  |  |  |
| --- | --- | --- | --- |
| Date | Version | Description | Author(s) |
| 5/23 | 0.01 | Draft document created for EDS 3 LFC Planning Test Period w/ Market Participants. This version is a working draft for planning discussion with Participants. | IRT |
| 7/23 | 0.02 | Draft Updated from meeting comments. | IRT and Operations |
| 9/12 | 0.03 | Draft updated from internal meeting comments | IRT, Operations and Settlements |

Table of Contents

1	Introduction	3

1.1	Market Participant Handbook	3

1.2	Document Structure	3

2	Release Overview	3

2.1	Early Deliveries	3

2.2	Nodal Sandbox	Error! Bookmark not defined.

2.3	Supporting Documents	3

3	R6.1  – ACE Calculation and Pre-Condition Validation	3

3.1	R6.1 Overview	3

3.2	EDS Testing Activities	3

3.3	Market Participant Involvement	3

3.4	Market Participant Systems Readiness	Error! Bookmark not defined.

4	R6.2 – Load Frequency Control (Individual QSE)	3

4.1	R6.2 Overview	3

4.2	EDS Activities	3

4.3	Market Participant Involvement	3

4.4	Market Participant Systems Readiness	3

5	R6.3 – Load Frequency Control (Total System)	3

5.1	R6.3 Overview	3

5.2	EDS Activities	3

5.3	Market Participant Involvement	3

5.4	Market Participant Systems Readiness	3

6	EDS Communications	3

6.1	EDS Planning Workshops	3

6.2	Online Readiness Center	3

6.3	EDS Kickoff Session	3

6.4	EDS Weekly Conference Calls	3

6.5	Weekly Status Bulletin	3

6.6	Issue Tracking Process	3

6.7	Entry / Exit Criteria	3

7	Appendix	3

7.1	Issue Submission Lifecycle	3

7.2	Draft Issue Submission Form	3

- Introduction

The ERCOT Nodal Transition Plan, approved by the Technical Advisory Committee (TAC), organizes transition activities into four tracks, which requires participation from both ERCOT and Market Participants (MPs). The Texas Nodal Program defined four Early Delivery Systems (EDS) sequences to meet the requirements of the Systems Testing and Nodal Market Implementation track of the Transition Plan. These sequences were further refined based on the Nodal project delivery schedules to group Nodal functionality and features into nine incremental software releases that will be used to meet the requirements outlined in the Nodal Transition Plan.

The EDS sequences and releases are outlined below:

EDS 1

- Release 1  –  Alarm Processing

- Release 2  –  Point-to-Point Checkout

EDS 2

- Release 3  –  Trial Operation of State Estimator & Network Security Analysis

- Release 4  –  Trial Operation of NMMS (Network Model Validation)

EDS 3

- Release 5  –  Trial Operation of SCED, 6 month LMP posting

- Release 6  –  Trial Operation of LFC, ACE			              (LFC Handbook)

- Release 7  –  Trial Operation of CRR, sample Settlement Statements

EDS 4

- Release 8  –  Trial Operation of RT Settlements (No Extracts)

- Release 9  –  Trial Operation of DAM, RUC, SASM, Full Settlements, EDW Extracts

- TXMACS 1.0  –  Full Nodal Functionality & 168 hour testing

Editors Note: There is no need to repeat all of this background information – We believe it wold be better to maintain the focus of the material in the LFC Handbook on the Release 6 test sequence.  An option here would be to include a link to the EDS3 web site that includes the Release 6 schedule etc.

## Market Participant LFC Handbook

The Market Participant LFC Handbook has been created to provide a detailed testing guide for participation in the Early Delivery System (EDS) activities. The Handbook is one of the guiding documents to help Market Participants understand how to prepare, participate and when to engage in EDS. This Handbook will cover the details for Release 6 – Load Frequency Control Testing. The LFC Handbook will be approved by the ERCOT Board and any subsequent changes that are made to the handbook necessary to support ongoing EDS3 Release 6 testing, will be reported to the ERCOT Board.

The testing areas described in this document will be guided by the Nodal Transition Plan and the Nodal delivery schedule; however, the detailed testing activities and schedule will be completed by working collaboratively with ERCOT subject matter experts and MP Representatives.

## Document Structure

It is critical that all participants have a common understanding of EDS activities, start dates, and participation expectations. This document will cover the following topics to ensure that ERCOT and MPs are ready for each EDS phase.

Release Overview – This section outlines the specific phases, objectives, and supporting documents for the Release 6 – Load Frequency Control Testing.

For Each Phase

- EDS Phase Overview

  - EDS Environment

  - Testing Schedule

  - EDS Functionality

- EDS Testing Activities

  - Testing Structure

  - Test Procedures

- Market Participant Involvement

  - Target Roles

  - Preparation Activities

  - System Readiness

  - Ongoing involvement

# EDS 3 Release 6 Overview

For EDS 3, LFC will be the second business functionality released to the EDS environment. The release procedure will follow the ERCOT release mechanism described earlier in this document. The initial system delivery will provide QSE’s and ERCOT the opportunity to validate the Nodal Generation Systems calculation of Area Control Error (ACE), Resource Limit Calculator (RLC), Emergency Base Point calculation, and the Ancillary Service Capacity Monitor (ASCM).  Later phases of Release 6 will also test the QSEs ability to follow LFC Regulation Dispatch Instruction with their Resources, control their Resources in Constant Frequency Mode, and finally, maintain ERCOT system frequency through the Nodal system control of Generation Resources and Controllable Load Resources.

All marketing activity during testing periods will be monitored by the Independent Market Monitor.

## Early Deliveries

The Trial Operations of LFC will be executed in three phases, validating pre-conditions before executing operational control over physical Resources deployment from the Nodal LFC/Generation Subsystem.  The Early Delivery System approach will allow ERCOT and MPs to begin testing as early as practical.

The following phases and objectives have been defined:

R6.1 - ACE Calculation and Pre-conditions

- Compare continuously for 7 days Nodal ACE results with Zonal ACE results for accuracy

- Validate completion of all communication system testing between ERCOT and QSEs with Resources

- Verify calculations of HASL, LASL, SURAMP, SDRAMP, HDL, LDL by the ERCOT Resource Limit Calculator

- Verify ability to calculate and issue Emergency Base Points to QSE’s

- Verify the ERCOT Ancillary Services Capacity Monitor

R6.2 - Load Frequency Control (LFC) Individual QSE testing

- Verify for each QSE and those Resources which the QSE has designated to provide Regulation Up Service and Regulation Down Service in the Nodal Market, the ability to provide Regulation Control on Nodal Systems.  EDS 3 testing will include only those Resources that are on-line in the Zonal market during the scheduled QSE test period.

- Verify for each QSE providing Regulation Service the ability to operate on Constant Frequency

R6.3 - Load Frequency Control (LFC) Total System testing

- Verify LFC’s ability to maintain system frequency with all QSEs and Resources providing Regulation Up Service and Regulation Down Service through Nodal Dispatch Instructions.

- Verify LFC’s ability to meet NERC control systems performance criteria

## Supporting Documents

The following documentation should be reviewed for a better understanding of the overall EDS 3 Approach, Market System Requirements, Generation Subsystem Requirements and ICCP specification details.

| Reference: Nodal Website | Description | Version |
| --- | --- | --- |
| Generation Subsystem | Texas Nodal Energy Management System Requirement Specifications For the Generation Subsystem | 1.0.0 |
| SCED Requirements | Texas Nodal Market Management Systems (MMS) Requirement Specification For SCED and Real-Time MMS Processes | 1.0.0 |
| ICCP Handbook | ERCOT Nodal ICCP Handbook | 1.0.0 |
| EDS 3 Approach Document | EDS 3 Approach Document | 1.0 |
| EMS Design | Texas Nodal EMS Conceptual System Design Document | 0.11 |
| EMS SCADA Requirements | Texas Nodal EMS Requirements Specification For SCADA | 1.0 |

# R6.1 - ACE Calculation and Pre-Condition Validation

## R6.1 Overview

EDS Environment

R6.1 will check the accuracy of the Nodal calculation of the ACE compared to the Zonal system for seven days.  R6.1 will also verify that the QSEs supporting Nodal ICCP systems can communicate with ERCOT Nodal ICCP systems and that other EMS upgrades of the Generation Subsystem have been completed.  The calculations performed by the Resource Limit Calculator (RLC) will be verified and testing will be carried out to confirm a QSE’s ability to receive Emergency Base Points.

The diagram below highlights the components tested during R6.1:

* Note: Only the colored components will be tested during phase R6.1.  Please revise the diagram per the following.  The SCED BP, UDBP, EMBP, REGUP and REGDN should indicate information flow from ERCOT EMS over ICCP to the QSE.  MW Output HSL/LSL etc should indicate information flow from the QSE to ERCOT over ICCP.  Additionally, please make clear that the functionality described in the box titled “5-min Resource Specific Base Point Schedule” is an artifice required only for the EDS 3 test sequence and is not part of the EMS or market systems.

The ERCOT applications deployed for phase R6.1 of LFC testing will be installed on ERCOT production hardware rather than testing hardware. These systems are intended to perform to ERCOT production standards for LFC testing.

In general, the EDS systems will be available and supported from 8am to 5pm on designated “EDS Testing Days” based on the defined EDS calendar. During off hours and non-testing days the system may be unavailable for system updates, ERCOT testing, or other testing activities. Any changes in testing schedules will be reflected in the EDS testing calendar and communicated to MPs.  However all the LFC testing phases will involve tightly coordinated activities between QSEs with Resources and ERCOT LFC testing personnel, the system will be available only to scheduled QSEs during their designated test times.

Testing Schedule

The ACE Calculation and Pre-Conditions Validation phase R6.1 is targeted to take place from January 2008 to the end of March 2008. During this period, QSEs should finish testing EDS2 back-end validation of communications capabilities.  This must happen prior to the QSE engaging in R6.2 testing activities.

The EDS team will provide a schedule of when ACE Calculations are being performed and compared to Zonal frequency calculation values.

The diagram below shows a typical EDS testing week:

Monday

Tuesday

Wednesday

Thursday

Friday

Monday Conf Call

Morning Test Period

Morning Test Period

Morning Test Period

Friday Conf Call

Channel: Conf Call

Channel: Conf Call

Channel: Conf Call

Channel: Conf Call

Channel: Conf Call

Audience: All QSEs

Audience: Single QSE and

team

Audience: Single QSE and

team

Audience: Single QSE and

team

Audience: All QSEs

Subj: Overview of weekly

activities

Subj: Support EDS

Activities

Subj: Support EDS

Activities

Subj: Support EDS

Activities

Subj: Review EDS progress

& issues

Afternoon Test Period

Afternoon Test Period

Afternoon Test Period

Channel: Conf Call

Channel: Conf Call

Channel: Conf Call

Audience: Single QSE and

team

Audience: Single QSE and

team

Audience: Single QSE and

team

Subj: Support EDS

Activities

Subj: Support EDS

Activities

Subj: Support EDS

Activities

- Monday Conference Call - Used to communicate with all EDS participants on

  - EDS activities planned for the week

  - Updates to online support documents & tools

  - Resolved issues or environment updates

- Mid Week Test Periods - The EDS support team will have two Test Period slots for each day Tue, Wed, and Thurs that Individual QSEs will have the opportunity to signup for support from ERCOT Subject Matter Experts to walk through EDS testing activities or work on specific QSE integration issues. A detailed calendar of EDS Test Periods will be available on the Nodal Website.

- Friday Conference Call - Used to communicate with all EDS participants on

  - EDS activities accomplished during the week

  - Updates to online support documents and tools

  - Identified software or environment updates

Results from the ACE Calculation Validation will be shared on the Monday and Friday “all QSE” conference calls.

EDS 3R6.1 Functionality

This section outlines the system interfaces, web services, and requirements functionality tested in phase R6.1:

Generation Subsystem Functionality (LFC)

The tables below describe the capabilities and requirement coverage of the initial EMS system to support input data validation, operations monitoring and control. The requirements documentation and specific details can be found on the Nodal Readiness Center Website.

ACE Calculations

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 1 | GS-FR2 | ACE Calculation |  |
| 2 | GS-FR3 | Regulation reduction |  |

Resource Limit Calculator

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 3 | GS-FR36 | Limit calculations |  |

Validation of Other Calculations

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 4 | GS-FR38 | Inputs from SCADA |  |
| 5 | GS-FR40 | Form of Resource Base Points |  |
| 6 | GS-FR43 | Data outputs to MMS |  |
| 7 | GS-FR44 | Database Entry |  |
| 8 | GS-FR48 | Emergency Base Points |  |

## EDS 3R6.1 Testing Activities

R6.1 tests the ERCOT Nodal software and communication without physically switching or controlling any Resources. Prior to these testing activities, all Nodal software and communication systems will have been tested in Factory Acceptance Testing (FAT) and ITEST leading to EDS3 and each QSE will have tested its Nodal EMS and communication systems.

Testing Structure

The following testing activities are required for phase R6.1 and will be coordinated by ERCOT:

- Comparison of the  Nodal ACE results with Zonal ACE results to test accuracy for a continuous 7 day period

- Verification of outputs produced by RLC for each QSE

- Verification of ERCOT’s ability to calculate and issue Emergency Base Points for each QSE

ACE Calculation Verification Test Structure

This test will be carried out as required by the ERCOT Nodal Transition Plan and will be performed solely by ERCOT.  No MP involvement during testing periods will be necessary.

The system ACE will be calculated by LFC using the following formula:

Raw ACE = Frequency Bias * (Actual Frequency – Scheduled Frequency)

The Frequency Bias will be equal to the ERCOT Area Frequency Bias in MW/0.1 Hz.  This value will then be compared for accuracy to the ACE calculation produced by the Zonal system.

ACE Calculation Verification Completion Criteria

To pass an ACE Calculation interval (4 seconds) the percentage difference between the Zonal ACE and Nodal ACE must be less than one percent. To complete the seven day continuous test, the Nodal ACE must meet the criteria for at least 98% of all valid intervals with no intervals having a difference greater than 50 MW.

Resource Limit Calculator and Emergency Base Point Verification Test Structure

All QSEs representing Resources should participate in this part of the LFC testing.  During the testing:

- Nodal LFC, Nodal ICCP, QSE EMS (Nodal) environments will be used for testing

- Test control signals will be sent from Nodal LFC to QSE EMS (Nodal)

- Only one QSE will participate at a time

- Each QSE will select several of its Resources with which to validate the ERCOT RLC calculations

- Input data for the RLC will be entered manually into the Nodal system by the QSE for that Resource

- ERCOT will verify that the RLC outputs update in accordance with the RLC design for each manual change by the QSE

- ERCOT will trigger an Emergency Base Point Calculation

- QSEs will verify that they have received both the Emergency Base Point and the status flag indicating that the base point was sent from the Emergency Base Point Calculator

Resource Limit Calculator and Emergency Base Point Verification Test Procedure

The following is the step by step description of the RLC verification approach:

Preconditions

- ICCP and the Generation Subsystem (LFC, RLC and Resource Qualification Testing) will have passed FAT and completed acceptable portions of the ITEST.

Before the Test

- QSEs will have provided ERCOT with a completed R6.1 Test Form in order to provide initial inputs for the QSEs’ Resources

During the Test

- ERCOT will ask the QSE to manually change SCADA data telemetry for the predetermined Resource.  The input data will be:

  - Output MW

  - Reg-Up Ancillary Service Resource Responsibility

  - Reg-Down Ancillary Service Resource Responsibility

  - Responsive Reserve Ancillary Service Schedule

  - Non-Spin Ancillary Service Schedule

How does this data by Resource get reconciled with the zonal QSE AS Responsibilities and Schedules?

- ERCOT will activate the Responsive Reserve deployment flag and verify changes to RLC calculations.

- ERCOT will verify the various output data produced by RLC.  The output data will be:

  - Resource High Ancillary Service Limit (HASL)

  - Resource Low Ancillary Service Limit (LASL)

  - Resource SCED Up Ramp Rate (SURAMP)

  - Resource SCED Down Ramp Rate (SDRAMP)

  - Resource High Dispatch Limit (HDL)

  - Resource Low Dispatch Limit (LDL)

- ERCOT will manually enter an Emergency Base Point Incremental MW value and trigger the Emergency Base Point calculation

- The entered Incremental MW value will then be distributed among the dispatchable Generation Resources in LFC.  The QSE under test will receive a new Base Point calculated from the Emergency Base Point calculator.  The QSE will also receive a status flag indicating that the Base Point has been provided by the Emergency Base Point Calculator

- The QSE will be asked to verify that its Resource Base Point has updated and that it has received the aforementioned status flag

After the Test

- ERCOT will verify that the RLC calculations and the Emergency Base Point for the Resource were correct.  These calculations will be done in accordance with the EMS Conceptual System Design document.

- ERCOT will verify the Nodal Ancillary Service Capacity Monitor calculations by comparing the results to the Zonal Ancillary Service Capacity calculations.  How will a comparison be done between zonal QSE AS responsibilities and schedules and nodal Resource AS responsibilities and schedules.

- The data captured and test results will be sent to the respective QSE.

- If a QSE cannot participate in or complete the testing during the scheduled time, it will be required to coordinate with ERCOT to reschedule a new test time.

RLC Calculation Verification Completion Criteria

The RLC verification for each QSE will be completed after each RLC calculation has been verified by ERCOT and the relevant QSE for correctness, and any outstanding issues related to the calculations have been adequately addressed.

Settlement Considerations for All R6.1 testing

- QSE Resource portfolios will be controlled by Zonal systems and will not be part of these tests

- No impact to Zonal settlements.

## Market Participant Involvement

Target Roles

The activities and functionality tested in EDS 3 are relevant to the following MP groups:

QSEs representing Resources:  ICCP Validations

ERCOT:  ACE calculation and Nodal ACE Comparison, other calculations

While there will be limited involvement necessary from the MPs for validation of the Nodal ACE calculation, participation in the other testing activities will be required before entering R6.2.  During the RLC calculation testing, the QSE will be involved in providing input data to ERCOT through the Nodal system.  During the Emergency Base Point testing, the QSE will be required to verify that it has received an Emergency Base Point Dispatch Instruction for a Resource.

Many MPs will be on different schedules. It is recommended that QSEs attend conference calls at least once a week, checking the Readiness Center for EDS 3 documentation updates during the entire period to keep updated on EDS activities, lessons learned, environmental changes, and overall progress.

Preparation Activities

No special training will be provided for participation in phase R6.1 of LFC Testing.

System Readiness

Not Applicable

Ongoing Involvement

There is a limited set of activities that should be completed at least one time to ensure connectivity and ability to receive outputs and control Resources. Once these are complete, MPs are encouraged to continue testing connectivity and Resource control thoroughly.  It is recommended that QSEs continue to attend the weekly conference calls even after their own testing for phase R6.1 has been completed.

# R6.2 - Load Frequency Control Individual QSE

## R6.2 Overview

EDS Environment

R6.2 will be an integrated test of major system components that include the ERCOT Nodal software, the communication from ERCOT to QSEs, the QSE Nodal system and communication from QSEs to physical Resources. The integrated test will be performed one QSE at a time, with the Nodal System calculating and sending Regulation Dispatch Instructions to the QSE under test while the Zonal System continues to send Regulation Service Dispatch Instructions to the remaining QSE’s not under test. The ERCOT Zonal and ERCOT Nodal systems will see the frequency deviations, calculate the same ACE, and dispatch Regulation asynchronously.

EDS3R6.2 will be accomplished with those Resources that are on-line in the Zonal Market and that the QSE has designated as cap[able of providing Regulation Service in the Nodal Market.  QSEs are not expect to bring off-line Resources on-line for the purpose of this test and are not expected to test every resource designated as capable of providing Regulation Service in the Nodal Market.  A QSE’s Resources being tested on Nodal will be asked to respond to LFC Regulation dispatch based on a pre-determined Ancillary Service obligation for the test period. The ability of the Resources to follow Nodal LFC Regulation Dispatch Instructions will be determined by monitoring the Regulation Dispatch Instructions, Resource’s Base Points, Resource’s Participation Factors and observed MW output of the Resources.

The Resource Qualification Testing software is a function within the Nodal EMS Generation System module and will be used to facilitate LFC testing.   The Resource Qualification Testing tool will provide the ERCOT Operator and Test Engineer the ability to track Resource response in Real Time on a Resource-specific basis and allow multiple Resources to be tested during a single test period with the goal of determining the general capability of LFC to send to the QSE, LFC Dispatch Instructions and for the QSE to deploy its Resources.  ERCOT will inform QSEs of any Resource’s questionable response to the LFC Dispatch Instructions. QSEs will be responsible for addressing Resource control problems identified prior to the start of nodal “go live” operations.

R6.2 also includes testing to verify that each QSE with Resources to provide Regulation Service in Nodal has the ability to operate on Constant Frequency on their Nodal systems.  This test will determine a QSE’s ability to correctly respond to system frequency changes.

The ERCOT and Market Participant applications deployed for phase R6.2 of testing will be installed on production hardware rather than testing hardware. These systems are intended to perform to production standards for LFC testing.

* Note: Only the colored components will be tested during phase R6.2.

Testing Schedule

The LFC Regulation and Constant Frequency Operation tests for individual QSEs are targeted to take place between March 2008 and May 2008.  Individual LFC testing for QSEs will be available after R6.2; however, these tests must be scheduled so they do not conflict or impede the continuing EDS3 programmed testing such as SCED testing, R6.3 of LFC testing, etc. Individual QSE testing of Resources not granted qualification through the attestation process should be completed before the start of the Nodal system. Each QSE participating in the LFC Regulation test will be scheduled for at least a one hour test period.  The test period time may be extended if additional testing time is required.  For QSE’s with a large portfolio of Resources providing Regulation Service, additional test periods may be scheduled to allow the QSEs to manage impact and risk.  ERCOT will scheduled and coordinate all test periods.

Testing a QSE’s ability to operate on Constant Frequency will be scheduled directly before or after the LFC Regulation test. The Constant Frequency test is to be coordinated with ERCOT and the time required for operating on Constant Frequency will be approximately 15 minutes.

EDS Functionality

Generation Subsystem Functionality (LFC)

The tables below describe the capabilities and requirement coverage of the EMS system to support input data validation, operation monitoring and control in addition to those listed in R6.1. The requirements documentation and specific details can be found on the Nodal Readiness Center Website.

LFC Resource Control

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 1 | GS-FR1 | Regulation without optimization |  |
| 2 | GS-FR4 | Reg-Up and Reg-Down allocation to QSE’s |  |
| 3 | GS-FR5 | Base Point Ramping and Permissive Blocking |  |
| 4 | GS-FR6 | LFC Performance |  |
| 5 | GS-FR7 | Regulation output control signals |  |
| 6 | GS-FR8 | Allocation of Regulation signals to individual Resources |  |
| 7 | GS-FR9 | Frequency selection |  |
| 8 | GS-FR37 | Reg and RRS Qualification Testing feature |  |

Ancillary Service Capacity Monitor

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 9 | GS-FR28 | Available ancillary service capacity by Resource |  |
| 10 | GS-FR30 | Ancillary service reserves |  |
| 11 | GS-FR32 | Average Generator regulation and Average MW output |  |
| 12 | GS-FR33 | Expected primary frequency response from Resources |  |
| 13 | GS-FR34 | Resource not responding Flags |  |
| 14 | GS-FR35 | Resource Error |  |

Resource Limit Calculator

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 15 | GS-FR36 | Limit Calculations |  |

Resource Qualification Testing

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 16 | GS-FR37 | Regulation and Responsive Reserve Qualification Testing Feature |  |

Generation Subsystem Inputs and Outputs

|  | Req | Req Specification Name | Description |
| --- | --- | --- | --- |
| 17 | GS-FR38 | Inputs from SCADA |  |
| 18 | GS-FR39 | Centralized Dispatch |  |
| 19 | GS-FR44 | Database Entry |  |
| 20 | GS-FR47 | Updated Desired Base Point |  |
| 21 | GS-FR49 | LFC Control Modes |  |

## EDS3R6.2 Testing Activities

The testing activities for R6.2 involve the physical deployment of Resources.  For this reason, all QSE testing activities will be coordinated with ERCOT and any deviation from the testing activities will need to be approved by ERCOT prior to the test date.

Testing Structure

Required testing activities:

- Individual QSE Regulation - verification that each QSE and selected Resources designated to provide Regulation Up Service and Regulation Down Service in Nodal has the ability to receive Nodal Dispatch Instructions and provide Regulation Control on their Nodal Systems.

- Constant Frequency Operation  - verification of each QSE’s ability to operate on constant frequency

Individual QSE Regulation Test Structure

QSEs Resources designated to provide Regulation Service in Nodal should participate in the LFC Regulation testing.  During the Individual QSE LFC Regulation tests:

- Each Regulation test period will be at least 1 hour per QSE.

- A QSE may continue to participate in Zonal Real Time Balancing Energy during the one hour test period only with Resources not participating in the LFC Regulation test.  Resources participating in the LFC Regulation test can not participate in Zonal Real Time Balancing Energy during the scheduled one hour test period.

- A five minute Resource-Specific Base Point Schedule must be provided for each Resource participating in the LFC Regulation test and must represent the Resource-Specific fifteen minute Zonal Base Point Schedule for the scheduled test period.

- The Resource-Specific Base Point Schedules must be provided to ERCOT in a specified format and can be adjusted up to 30 minutes before the scheduled test period start time.  If the QSE elects to maintain Ancillary Service Capacity on the Resource undergoing test, it must accommodate such capacity in the construction of its Base Point Schedules.

- The five minute Resource-Specific Base Point Schedules should not be adjusted during the test period.

- ERCOT or the QSE may terminate testing for system operations considerations at any time.

- A VDI will be issued for the QSE participating in the test, which will be valid only for the test period, and provide the QSE exemptions from Uninstructed Resource Charge and Schedule Control Error settlement charges and the exclusion of non-compliant CPS1 intervals.

Individual QSE Regulation Test Procedure

The following is the step-by-step description of the LFC Regulation test:

Preconditions

- ICCP and the Generation Subsystem (LFC, RLC and Resource Qualification Testing) will have passed FAT and completed acceptable portions of the ITEST.

- QSEs will have tested and demonstrated that communication from their EMS (new or significantly changed) to their Resources is functional.

- QSEs will have tested the ability to provide Resource-Specific five minute Base Point Schedules to ERCOT.

- QSEs will have tested the capability to obtain Regulation Service Dispatch Instructions from both the ERCOT Zonal and Nodal system and be able to switch between the Zonal and Nodal systems within two minutes of receiving an instruction from ERCOT via a hot line call.

- Both the ERCOT Zonal and Nodal systems will have the capability to obtain system frequency simultaneously.

- QSEs under test will have the capability to continue to provide data to the ERCOT Zonal system.

- ERCOT will have a LFC monitoring tool to enable the testing of multiple Resources within a single QSE.  Is this the EMS Resource Qualification tool?

Before the Test

- ERCOT will confirm the test date and time with the QSE at least two days in advance.  ERCOT shall make good faith efforts to accommodate QSE requests to schedule the test to minimize the impact of the test on the QSE’s fleet operations.  In order to complete testing within the project schedule time line, QSEs shall make a good faith effort to accommodate the agreed upon test schedule.  The following rules shall be applied for Resource / QSE selection for testing:

Where practical, the QSE will have been awarded Regulation Service from the Zonal Day Ahead Ancillary Services Market or Self-arrange Regulation Service on its Resources to participate in LFC testing.

- The QSE under test will participate in the Zonal Ancillary Services Market. The hourly ratio of the Regulation Service obligation of the QSE under test to the total hourly ERCOT requirement will be the same in the Nodal LFC during testing. These ratios will be available after the Zonal Ancillary Service Market clears.

- The QSE under test must submit Resource-Specific five minute Base Point Schedules to represent the Resource-Specific fifteen minute Zonal Base Point Schedules for the scheduled test period.  This will be used as the SCED Base Point input for the LFC calculations and will be sent to ERCOT at least 30 minutes before the start of the test period.

During the Test

ERCOT will begin the test by issuing a VDI.  If at any time during the test either ERCOT or the QSE terminates the test, ERCOT will issue a VDI documenting the termination event.  ERCOT will end the test by issuing a VDI documenting the end of the test and instructing the QSE to return to control under the Nodal System.

- ERCOT will input into the Nodal system the Resource’s Base Points provided by the QSE at five minute intervals.

- ERCOT will input the Regulation Up and Regulation Down obligation of the QSE under test into the Nodal system.

- At the scheduled hour, the test will start or, if system conditions do not permit the test, may be delayed or aborted as necessary. ERCOT will select the QSE under test to Zonal ‘test’ mode. Please explain the meaning of zonal “test” mode.  Please clarify the status of the QSE with regard to Zonal Regulation.  Luminant suggests that the easiest approach would be to move all of the QSE’s zonal Regulation Responsibility to the nodal LFC for the purpose of this test.  This will effectively result in the QSE’s Reg-Up and Reg-Dn obligation in zonal to be equal to 0 during the test period.

- The QSE will switch the Resources being tested to receive Regulation Service instructions and be controlled from the ERCOT Nodal system.

- For each Resource under test, the QSE must telemeter a Resource participation factor greater than zero for test period.

- The Nodal LFC will compute the required Regulation and the Updated Desired Base Point using the five minute Resource-specific Base Points provided by the QSE, the telemetered Regulation Participation Factors, the system frequency and the AS obligation’s, and send the Dispatch Instructions to the QSE under test via ICCP.

- The Zonal system will continue to compute and send the required Regulation Service Dispatch Instructions to all QSE’s, including the QSEs under nodal testing. During the test period, the QSE being tested should ignore the Regulation Dispatch Instructions from the ERCOT Zonal system.

- If a determination is made that a Resource is not responding to Nodal LFC Dispatch Instruction appropriately, that Resource will be excluded from the test and, if necessary, the test will be discontinued and control will be returned to the Zonal system.

- At the end of the hour, under direction from ERCOT, the QSE under test will switch control back to Zonal and conclude the test or continue to operate on Nodal system for the Constant Frequency Operation test if so directed by ERCOT.

- On the completion of all testing, ERCOT will remove the QSE under test from Zonal ‘test’ mode.

After the Test

- All test data will be compiled for the QSE and each Resource tested.

- ERCOT will determine if each Resource tested responded to the Dispatch Instructions provided by the Nodal LFC.   The ability of Resources to respond to Nodal LFC in controlling system frequency will be used to gauge the readiness of the Nodal system.

- QSEs inappropriately responding to the Nodal LFC Regulation test, as defined by the criteria below, will be required to re-schedule another test period.

Settlement Considerations

- QSEs under test will not be subject to Uninstructed Resource Charges (URC) of Schedule Control Error (SCE) for the hour before the test period, during the test period and the hour following the test period.

- Verbal Dispatch Instructions (VDI) records will be sent to the ERCOT Settlement group for the hours the QSE participated in LFC Regulation testing.

- For periods not covered by the VDI, all URC and SCE will apply.

Individual QSE Regulation Completion Criteria

- Successful Market Participant Readiness will be based on the QSE’s ability to receive Regulation signals from ERCOT and to distribute Regulation control signals to the Resources under test; and on the changes in the Resources power output consistent with the QSE Regulation control signals.

- ERCOT shall provide the QSE the output from the EMS Qualification Tool for each Resource tested. ERCOT shall also provide a calculation of the one minute average of the absolute difference between the Resource’s actual MW and the Expected MW output where the Expected MW output equals the sum of the Updated Desired Base Point MW and Regulation requested MW value.  ERCOT and the QSE shall jointly evaluate each Resource’s performance during the test by comparing the Resource performance to the AS qualification criteria for Regulation Service in Nodal Protocol Section 8.

Constant Frequency Operation Test Structure

All QSE’s with Resource(s) to provide Regulation Service in Nodal should participate in the Constant Frequency Operation testing. The testing is planned to be done immediately before or after the LFC testing while QSE’s are operating on their Nodal system.

Constant Frequency Operation Test Procedure

The following is the step-by-step description of the Constant Frequency testing:

- QSE will switch (or be already switched) to their Nodal system.

- ERCOT will request the QSE to switch to Constant Frequency operation.

- The QSE will operate on Constant Frequency for at least 15 minutes

- ERCOT will request the QSE to cease operating on Constant Frequency mode and return to following Regulation Service Dispatch Instructions from ERCOT Nodal System

Constant Frequency Operation Completion Criteria

ERCOT will monitor QSE and individual Resource response to system frequency to evaluate QSE performance for purpose of meeting Nodal Readiness Criteria.

## Market Participant Involvement

Target Roles

The activities and functionality being tested in EDS 3 are relevant to the following MP groups:

QSE’s representing Resources which are providers of Regulation Service in Nodal:  QSE receipt of instructions and Resource response.

ERCOT:  Dispatch Instruction and Resource monitoring

Preparation Activities

ERCOT will define a test calendar similar to the one used for Point-to-Point and SCED testing   MP’s will be required to sign-up for test periods.

Many MPs will be on different test schedules. MPs should participate in the conference calls at least once per week, checking the Nodal Readiness Center website for EDS 3 documentation updates during the entire period to keep updated on EDS activities, lessons learned, environmental changes and overall progress.

The QSE shall coordinate its LFC Regulation and Constant Frequency testing with ERCOT.  This is mandatory testing for QSEs to participate in R6.3 testing as Regulation Service provider.

Systems Readiness

MPs’ systems must be able to receive Regulation Dispatch Instructions from the ERCOT Nodal System.  MPs must be able to provide Resource-level five minute Resource-specific Base Point Schedules to ERCOT. MPs’ Nodal EMS system must be able to receive ERCOT Regulation Service Dispatch Instructions, regulate Resources as instructed and operate on Constant Frequency.

Ongoing Involvement

There is a limited set of activities that should be completed at least one time to ensure connectivity and ability to receive outputs and control Resources. Once these are complete, MPs are encouraged to continue testing connectivity and Resource control thoroughly.  It is recommended that QSEs continue to attend the weekly conference calls even after their own testing for phase R6.2 has been completed.

# R6.3 - Load Frequency Control (Total System)

## Eds3R6.3 Overview

EDS Environment

R6.3 will test ERCOT’s ability to maintain system frequency using the Nodal system for Regulation Service and meet the NERC frequency control criteria using nodal systems software. Phase R6.3 will include three tests and will involve all QSEs that have completed R6.2 LFC testing. The three tests will have duration periods of two, eight and forty-eight hours, respectively.  The first two tests will allow ERCOT and QSEs to build confidence in the Nodal system in controlling both Balancing Energy and frequency. The forty-eight hour test will ensure the Nodal system is exposed to a complete ERCOT load profile and allow any outstanding ERCOT or QSE issues to be addressed during the test. The Zonal system will continue producing Balancing Energy (BE) Dispatch Instructions and Regulation control requests; however BE and Regulation Service will be managed by the Nodal system. Both the Zonal and Nodal systems will see the frequency deviations, calculate the same ACE, have the same constraints activated and control at the same time.  The QSEs providing Regulation Service in Nodal will receive Dispatch Instructions based on the awarded Regulation Service in the Zonal Regulation self-provision and the Zonal AS Regulation market for the test period.  QSEs not participating in Regulation Service testing in R6.2 cannot provide Regulation Service in the Nodal system in R6.3 testing nor may they participate in the Zonal Regulation AS self-provision and AS Regulation market for the days in which nodal testing is scheduled.

All QSEs must follow the SCED calculated Base Point and the LFC Updated Desired Base Point.  QSEs must provide Energy Offer Curves and Output Schedules to SCED, as well as continue to provide energy schedules to the Zonal market for all hours during the test period.  Therefore, QSE’s will be operating parallel in both Zonal and Nodal in Real-time.

The Energy Offer Curves provided by the QSEs during the LFC testing shall be representative of the same QSE portfolio Balancing Energy Service bids submitted in the Zonal System.  The individual Resource Offer Curves should effectively be the same as those the QSE would use to individually dispatch its own Resources assuming it were accepting control from the Zonal system.

The Zonal system will continue to operate as normal and calculate MCPE’s for each Congestion Zone based on the QSE’s submitted BE Service bids.  However, SCED will manage energy balance and will provide Resource-Specific Base Points for all Resources using Energy Offer Curves or Output Schedules provided by the QSE.  ERCOT will not activate instruction in Zonal due to the Commercially Sensitive Constraints (CSC), but will manage CSCs and congestion through SCED Base Point calculation using local congestion methods.  ERCOT will activate the same constraints for local congestion management in the Zonal Real Time Constraint Activity Management (RTCAM) and Nodal Transmission Congestion Management (TCM) to ensure the MCPE prices determined by the Zonal System are accurate and suitable for settlements for the testing periods.

The ability of ERCOT to control frequency with the Nodal LFC will be gauged by NERC CPS criterion.  The CPS scores are calculated and monitored in the ERCOT EMS system. Regulation Service Dispatch Instructions, Resource Base Point, Resource Participation Factors and observed MW output of the Resources will be monitored and recorded for verifying ERCOT performance. The Resource Qualification Testing software is a function within the Nodal EMS Generation System module and will be used to monitor the performance of QSEs and Resources during the tests.

* Note: Only the colored components will be tested during phase R6.3.

EDS3R6.3 Testing Schedule

The integrated Total System LFC tests are targeted to take place starting in June 2008.  The scheduled date for the first test will depend on the completion of R6.2 testing and will require a a predetermined minimum amount of system Resources to have been tested in R6.2 and shown to have the ability to provide Regulation Service for Nodal.  In order to maintain the integrity and reliability of the ERCOT System and to test the LFC system’s ability to maintain system frequency through Regulation, R6.3 will include at least three tests of  two, eight and forty-eight hours each.  R6.3 testing will be scheduled during ERCOT System conditions favorable to testing with limited exposure to significant transmission congestion.  After the first (two hour) test, a complete evaluation of results will be conducted and reported to MPs. Similarly, on completion of the eight hour test, an evaluation of results will be provided to MPs prior to scheduling the forty-eight hour test. During the testing periods, ERCOT may abort the test at any time for any reason and immediately resume energy dispatch using the Zonal systems.  All R6.3 operations will be conducted under the direction of the ERCOT Shift Supervisor and QSE dispatch controller/operators.

R6.3 will use SCED to calculate and provide Resource-specific Base Points and will manage congestion and real time energy balancing.  QSEs must provide and update their Resource Energy Offer Curves and Output Schedules to ERCOT for SCED to calculate the Base Points.  LFC will use the SCED Base Points and will calculate an Updated Desired Base Point for each Resource, as well as the Regulation required.

EDS3R6.3 Functionality

Phase R6.3 of LFC testing will enable ERCOT and QSEs to perform frequency control through Regulation Service deployment and to view the outputs generated by LFC. All previous EMS system requirements for R6.1 and R6.2 will be required for R6.3 testing.  Also required are the MMS systems and functionalities to support the SCED process for both QSEs and ERCOT.

## EDS3R6.3 Test Activities

The testing activities for R6.3 involve the physical deployment of Resources.  For this reason, all testing activities will be coordinated with ERCOT and any deviation from the testing activities will need to be approved by ERCOT prior to the test date.

EDS3R6.3 Testing Structure

Required testing activities:

- Total System: - verify ERCOT ability to control frequency by dispatching Regulation Service with Nodal systems.

Total System Test Structure

All QSEs representing Resources must participate in the Total System test.  All QSEs must follow Base Points calculated from SCED.

- There will be multiple total system tests (a minimum of three).

- SCED will calculate Resource Base Points.

- LFC will calculate the Update Desired Base Points and the Regulation Service requirements for Resources and QSEs.

- QSEs must be able to switch back and follow Dispatch Instructions from the ERCOT Zonal system if instructed by ERCOT to do so.

- During the test period, the QSEs will not be subjected to URC in the same manner as in R6.2 testing.

- ERCOT’s Settlement group will use calculated MCPE’s from the Zonal system and OOME Dispatch Instructions from the Zonal system.

- A VDI will be issued for all QSEs participating in the test, which will be valid only for the test period, and provide each QSE exemptions from Uninstructed Resource Charges and Schedule Control Error settlement charges and the exclusion of non-compliant CPS1 intervals.

Luminant believes that conceptually the proposed Total System Test described here is doable.  We also believe that much more work is needed to completely define the test.  Many of the issues that need to be vetted by ERCOT and the Market Participants are deep level details, such as the use of consistent shift factors between the zonal settlement calculations and the nodal systems SCED dispatch.  Luminant suggests the need for a series of planning meetings to completely define the test structure and procedures,

Additionally, Luminant suggests that ERCOT and the Market Participants consider the use of a Real Time indicator that would be used to trigger test termination, if necessary.  For example, a running comparison of the Zonal MCPE for each zonal load zone to the comparable Load Zone SPP could be made with the requirement that a price separation in excess of a predetermined amount would require test termination.  The idea is to limit settlement intervals subject to such price separation and to determine the reason for the price separation and allow updates to the test procedure before proceeding with the test.

Total System Test Procedure

This initial portion of each test period is based on the expected time needed to select each QSE participating in Nodal testing, one by one, to verify frequency QSE performance in response to the SCED and LFC instructions.  Once all QSEs participating in the test have been selected, an additional fifteen minutes is required to control system frequency and capture testing data for performance analysis and reporting.  The eight and forty-eight hour tests will also follow the same initial switching from Zonal to Nodal as the two hour test.

The following is the step-by-step description of the Load Frequency Control Total System test:

Preconditions

- ICCP and the Generation Subsystem (LFC and Resource Qualification Testing) will have passed FAT and completed acceptable portions of the ITEST.

- ERCOT systems and QSEs providing Regulation Service will have participated and completed R6.2 Individual QSE LFC Regulation testing.

- All QSEs must be able to provide Energy Offer Curves and Output Schedules and all other information to support the SCED functionality. The Energy Offer Curves must be representative of the QSE Zonal Portfolio Offers.

- All QSEs will be able to respond to SCED Base Points and LFC Updated Desired Base Points on their Nodal systems.

- QSEs will continue to operate and provide data to ERCOT Zonal system.  QSEs will continue to receive data from the ERCOT Zonal system but will ignore this data during the test period unless ERCOT specifically instructs them to operate from the Zonal system.

- QSEs have the capability to obtain Base Points and Regulation Service Dispatch Instructions from the Nodal system or Balancing Energy Service Dispatch Instructions, OOME Dispatch Instructions and Regulation Service Dispatch Instructions from the Zonal system.  QSEs should be able to switch between them in less than two minutes.

- Both ERCOT Zonal and Nodal systems will have the capability to simultaneously obtain system frequency.

- Initial LFC tuning parameters shall be established by simulation testing, approved by the LFC Test team and reviewed by the PDC sub-committee of the ROS.

- ERCOT shall verify that the Nodal System Generation Control System, Network Security Analysis, Reserve Calculations, System Generation and Load Calculations and other critical operations functions reasonably track the same dispatch functions as the Zonal system given similar operating inputs. This will be done prior to scheduling the R6.3 testing.

Before the Test

- ERCOT will confirm a three day test window with the MPs at least two days before the first possible test date. ERCOT will then notify MPs of the actual test time at least one hour before the commencement of the test. ERCOT will issue a VDI to document the test initiation and ending events and will issue a VDI in the event that a test is prematurely terminated.  The following shall apply for EDS3R6.3 testing:

  - All QSEs representing Resources will participate in the EDS3R6.3 LFC Total System test.

  - LFC will send Dispatch Instructions according to the awarded Regulation Service from the Zonal Self-provision or Zonal AS Market.

  - All QSEs will follow SCED-calculated Base Points and the LFC-calculated Updated Desired Base Points.

- QSEs participating in the test may participate in the Zonal AS Markets. The hourly ratio of the Regulation Service obligation of the QSEs to the total hourly ERCOT requirement will establish the Regulation Service deployment in the R6.3 test.   This ratio will be available after the Zonal AS Markets clear. How will the QSE AS obligation be split among the QSE Resources for calculation of Resource limits?

- QSEs will participate in the Zonal Real Time Balancing Energy Market during the schedule test period as during normal zonal operations except that QSEs will ignore the BE Service Dispatch Instructions from the Zonal system and follow the test Base Points from the Nodal systems.  SCED will manage congestion and energy balancing.

- ERCOT shall declare its reasonable satisfaction that the Nodal Systems are emulating the actions of the Zonal System prior to starting the test.

During the Test

- At the scheduled hour, the test will start and, if system conditions do not permit, ERCOT will cancel the test.

- For each hour of the test, ERCOT will input the Regulation Service obligation of each QSE into the Nodal system.

- ERCOT will sequentially request QSEs to switch to Nodal systems and follow SCED Base Points and LFC Regulation, switch the QSE’s Resources to Zonal ‘test’ mode, and verify the continued correct operation of Regulation and frequency control.  Before proceeding to the next QSE, ERCOT will observe the operation of system frequency control and determine if it can safely add additional QSEs to the Nodal System control.  ERCOT Operations will continue to add QSEs until all Balancing Energy and Regulation Service is being controlled by the Nodal Systems.

- The Zonal System will continue to receive the system frequency and compute and send the Dispatch Instructions to all QSEs.

- At the discretion of ERCOT Operations, if system frequency is not being effectively controlled, the test will be immediately discontinued and the Resources will return to Zonal control in an orderly sequence as directed by ERCOT Operations.  If a significant frequency deviation occurs during the test, QSEs will be instructed by hot line call on specific actions to take.

- At the end of a test period, QSEs participating in the total system test will switch the control back to Zonal in the order as instructed by ERCOT to conclude the test.  This will be performed one QSE at a time.

- ERCOT will remove the ‘test’ mode from each of the QSEs under test in the Zonal system.

After the Test

- The Base Points, Regulation Service requested, Participation Factors, system frequency and Resource actual MW outputs will be compiled for the QSEs and for each Resource.

- ERCOT will analyze the results of the test and report to MPs its findings. Additional tests will be rescheduled by ERCOT as required.

- The Performance Disturbance Compliance committee will be invited to review the test results.

Settlement Considerations

- During the test period, ERCOT will settle transactions based on the Zonal Protocols using MCPEs calculated in the Zonal Market.

- MPs will continue to update their Resource Plans and Base Power Schedules during the test periods.  The constraints activated in Zonal RTCAM will also be active in Nodal TCM.  MPs shall continue to update their Zonal schedules and Balancing Energy Service offers.  During the test, QSEs should follow the Base Points provided by the Nodal system and ignore the OOME Dispatch Instructions from the Zonal system.  Units deployed by the Zonal Market for OOME and Local Balancing Energy will have their instructed output levels replaced with SCED Base Points,

- QSEs under test will not be subject to Uninstructed Resource Charges (URC) or Schedule control Error (SCE) for the hour before the test period, during the test period and the hour following the test period.

- Verbal Dispatch Instructions (VDI) records will be sent to the ERCOT Settlement group for the hours the QSE participated in LFC Regulation testing.

- If the test is discontinued and Resources are returned to Zonal control, then URC and SCE will apply following the first full hour of resumed zonal operations.

Nodal Completion Criteria for LFC Total System test

The completion criteria for each Total System test will be gauged on the following criteria:

- The rolling CPS1 one minute average score must equal or exceed 100% during the test period.

- The rolling CPS2 ten minute average score must equal or exceed 90% during the test period.

## Market Participant Involvement

The activities and functionality being tested in EDS 3 are relevant to the following MP groups:

QSE’s representing Resources which are providers of Regulation Service in Nodal:  QSE receipt of instructions and Resource response.

ERCOT:  Dispatch Instruction and Resource monitoring

Preparation Activities

Recommend MPs attending conference calls at least one time per week, checking the Readiness Center for EDS 3 documentation and schedule updates during the entire period to keep updated on EDS activities, lessons learned, environmental changes, and overall progress.  ERCOT will coordinate the R6.3 tests with participating QSEs.

Systems Readiness

MPs systems must be able to receive Regulation Dispatch Instructions from LFC and the ERCOT Nodal System. MPs must be able to follow five minute SCED Base Points and four second LFC Updated Desired Base Points. MPs must be able to provide Resource Energy Offer Curves and Output Schedules and any other supporting data for the SCED functionality.

Ongoing Involvement

There is a limited set of activities that should be completed at least one time to ensure connectivity and ability to receive outputs and control resources. Once these are complete, MPs are encouraged to continue testing connectivity and Resource control thoroughly.  It is recommended that QSEs continue to attend the weekly conference calls even after their own testing for phase R6.3 has been completed.

# EDS Communications

To ensure that Market Participants are kept abreast of the developments before and during the EDS testing, ERCOT has designed the following communication channels

## EDS Planning Workshops

To ensure that ERCOT and the MPs maximize the benefits of the EDS, starting in May 2007, the EDS team will schedule monthly planning Workshops and ongoing conference calls to complete the details required for EDS execution. The Workshops will focus on: (i) test preparations; (ii) testing scenarios; (iii) detailed test procedures and schedule of the test sequences; (iv) test sequence planning at the QSE and Resource level; (v) a substantive list of specific entry and exit criteria for each EDS Release; and (vi) the final exit criteria signifying the completion of all Transition Plan activities supporting a declaration of readiness. The EDS planning Workshops will provide input for the test plans and test scenarios to support the day-to-day testing activities.

## Online Readiness Center

Online readiness support for the ERCOT and MP transition to the Nodal market, as well as supporting EDS documentation, can be found in the Nodal Transition Readiness Center on the ERCOT Nodal Website: http://nodal.ercot.com/readiness/index.html

## EDS Kickoff Session

Channel: Meeting (Austin)

WebEx Audience: NTPM, EDSC

Timing: 3 weeks before EDS start

Materials: Agenda, EDS Handbook

Notes: Cover the following:

• Pre-EDS preparation activities that should be nearing completion

• Review enrollment process for preliminary testing

• Review how MPs will be able to access systems

• Q&A

• After meeting, post meeting notes, Q&A, presentation on web

## EDS Weekly Conference Calls

Channel: Conference Call

Audience: Participating MPs

Timing: TBD

Materials: TBD

## Weekly Status Bulletin

Channel: Market Notice, web

Audience: EDSC, NTPM

Timing: End of test week

Materials: Weekly status bulletin

Notes: Covers weekly status during formal testing. Interim bulletins may be sent as needed.

## Issue Tracking Process

Prior to the delivery of market systems and associated business functionality to the EDS environment, each computer application will be run through a series of testing phases to identify and resolve as many defects as possible. Some of the testing phases include Pre-FAT that would be done at the vendor site, Factory Acceptance Testing (FAT) that would be executed at ERCOT and finally Integration Testing (ITest) aimed to integrate testing all Nodal applications. Defects identified during these phases would be logged and tracked internally for resolution.  Given the accelerated release of many of the systems into the EDS environment and the gradual increase in quality of systems, it is anticipated that there will be defects discovered by the MPs.  These defects should be reported to ERCOT using a MP Issue Reporting Form (sample in appendix).   All items will be investigated by ERCOT testing personnel and logged into the internal defect tracking system.  Defect statuses will be discussed at the end of the week wrap-up call as well as posted on the Nodal Readiness Center website which will be updated weekly (process overview in appendix- TBD)

## Entry / Exit Criteria

To begin and end each of the EDS 3 Releases, a defined set of entrance and exit criteria must be defined to ensure readiness. Specific criteria will need to be defined for ERCOT and the MPs to help ensure that the test phase will be productive. During the market trials planning phase, the team will be working with MPs to finalize a set of measurable criteria.

# Appendix

## Issue Submission Lifecycle

## Draft Issue Submission Form