DRAFT COPY FOR REVIEW USE ONLY

Includes Comments from 9/24 ROS/Telemetry Standards Workshop

Reliant Energy Comments – September 28, 2007

Texas Nodal Market

Telemetry Criteria

Version 0.08

September 24, 2007

# Introduction

TAC is charged by the Nodal Protocol 3.10.7. 5 to create Telemetry Criteria. This Telemetry Criteria document specifies the Telemetry Criteria called for in the Nodal Protocols.  TAC approves the Telemetry Criteria and an appropriate TAC subcommittee is required to update the Telemetry Criteria annually each October or more often on a periodic basis as deemed necessary.

Acquisition of status and analog measurements of the transmission power system together with an accurate power system model of the system are processed by a State Estimator to provide an optimal estimate of the power system state at a given point in time while filtering measurement noise  and detecting gross errors. The quality and availability of telemetry provided to ERCOT are important to the performance of the ERCOT State Estimator and LMP  and price calculations as well as other all ERCOT Real-time applications.

In case of a conflict between these Telemetry Criteria and the Nodal Operating guide or the Nodal Protocols, the Nodal Protocols shall prevail.

# Requirements

## Operations Requirements

Telemetry of Breaker and Switch Status [NP: 3.10.7.5.1(1))]

Each TSP and QSE shall provide telemetry, to ERCOT on the status of all breakers and switches used to switch any Transmission Element or load modeled by ERCOT.  Each TSP and QSE is not required to install telemetry on individual breakers and switches, where the telemetered status shown to ERCOT is current and free from ambiguous changes in state caused by the TSP or QSE switching operations and TSP or QSE personnel.  Each TSP or QSE shall update the status of any breaker or switch through manual entries, if necessary, to communicate the actual current state of the device to ERCOT, except if the change in state is expected to return to the prior state within one minute.  If in the sole opinion of ERCOT, the manual updates of the TSP or QSE have been unsuccessful in maintaining the accuracy required to support State Estimator performance to the State Estimator Performance Standard, ERCOT may request that the TSP or QSE install complete telemetry from the breaker or switch to the TSP or QSE, and then to ERCOT.  In making the determination to request installation of additional telemetry from a breaker or switch, ERCOT shall consider the economic implications of inaccurate representation of Model Loads in LMP results  versus the cost to remedy.[ the above is quoted directly from the protocols and should not be changed]

Required TSP Telemetry [NP: 3.10.7.5.2]

TSPs are required to provide power operation data to ERCOT as defined in the ERCOT Nodal Protocols.  Each TSP shall provide telemetered measurements on modeled Transmission Elements to ensure State Estimator observability of any monitored voltage and power flow between their associated transmission breakers needed in achieving the TAC-approved State Estimator performance standard. On monitored non-Load substations, each TSP shall install, at the direction of ERCOT, sufficient telemetry such that there is an “N-1 Redundancy.”  An N-1 Redundancy exists if the flow remains observable on the loss of any single measurement pair (MW, MVAR) excluding station communication path failures.

- TSPs are required to provide power operation data to ERCOT as defined in the ERCOT Protocols and Nodal Operating Guides. ERCOT will monitor the validity of the Network Model as it affects State Estimator results in order to determine additional required data.

Non-TSP substation owners shall provide the required data to their interconnected TSP in accordance to new construction and redundancy  requirements set forth in R14 and R15.  If the data cannot be obtained, ERCOT shall report such cases to the Wholesale Electric Market Monitor (WEMM).

- Required QSE Telemetry [NP: 6.5.5.2(2)]1

QSEs are required to provide power operation data to ERCOT as defined in the ERCOT Nodal Protocols.

- Telemetry Scan Rates [NP: 3.10.7.5(3)]

ERCOT will scan QSE and TSP data at scan rates as defined in the ERCOT Nodal Protocols and the ERCOT Nodal Operating Guide.

The telemetry provided to ERCOT by each TSP must be updated at a 10 second or less scan rate and be provided to ERCOT at the same rate.  Each TSP and QSE shall install appropriate condition detection capability to notify ERCOT of potentially incorrect data from loss of communication or scan function.  Condition codes must accompany the data to indicate its quality and whether the data has been measured within the scan rate requirement.

- Data Quality

Market Participant’s shall provide documentation to ERCOT describing their native system quality codes and defining the conversion of their quality codes into the ERCOT defined ICCP quality codes consistent with the ERCOT Nodal Operating Guide.

## Maintenance Requirements

Minimum Telemetry Criteria [NP: 3.10.7.5.2(5)]

The TSP shall assist ERCOT in maintaining the algebraic sum of the telemetered measurements around each substation bus such that they are less than 5% of the largest normal line rating or 5 MW, whichever is greater.

- Telemetry Availability

All points made available to ERCOT must achieve a calendar quarterly availability of 99% percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with VALID quality codes at the scheduled periodicity. [ 80% allows data to be out of service for over 18 days in a calendar quarter; % availability must be at least consistent with Good Utility Practice.]

Where:

A =	average percent availability of all points received from a given QSE or TSP.

T =	total number of seconds in the quarter.

i =	the ith point having a quality code other than VALID

n =	total number of points having a quality code other than VALID

Bi =	number of seconds during the quarter that the ith point had quality other than VALID.

*Exceptions to Telemetry Availability calculation inputs:

- ERCOT declared Emergency Notice that can effect telemetry

- Total failure of the ERCOT WAN communication system

- [TSPs and QSEs must contract with 3rd parties to provide service to meet this standard; such is not under the control of ERCOT nor other MPs effected by the failed communication system]

- Locally and Remotely Replaced Telemetry

In the event that ERCOT identifies an individual Valid telemetered value which it believes is incorrect, it shall notify the providing entity, and direct them to manually replace the erroneous data until the error is corrected.

ERCOT will not manually replace telemetry status or analogs from TSP’s or QSE’s unless the TSP or QSE notifies them that they are technically incapable of performing a manual replace function due to technical difficulties at their facility except in emergency situations as deemed by the ERCOT shift supervisor.  In this event, ERCOT shall notify market participants thru the Event Notification System (ENS) until the technical difficulty is resolved.

Telemetry remotely replaced by TSP or QSE will be reported to the responsible owner.  When requested by ERCOT, TSP and QSE shall provide ERCOT with a plan within 2 Business Day for fixing  remotely replaced telemetry.

- Critically Important Telemetry

ERCOT will identify MW/MVAR Telemetry pairsand voltage points that are “critically important” to reliability, to system, generation, and load observability, to support of State Estimator performance, or are of a commercial Market concern.  This telemetry will be considered “Critically Important Telemetry” in the context of this document.

ERCOT will use the following criteria to identify critically important Telemetry:

(1)	Telemetry necessary to meet the requirements of the protocols.

(2)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a transmission line operated at 345 kV or above.

(3)	Loss of a telemetry point that results in the inability of ERCOT to monitor loading on a 345/138 kV autotransformer.

(4)	Loss of a telemetry point that results in the inability of ERCOT to monitor the loading on transmission facilities designated as critically important to transmission reliability by ERCOT. A list of critical facilities will be published annually.

(5)	Telemetry necessary to monitor transmission elements identified as causing 80% of congestion cost in the year for which the most recent data is available.

(6)	Telemetry necessary to monitor the 20 most voltage critical buses designated by ERCOT and approved by TAC each October.

- Availability for Critically Important Telemetry

All Critically Important Telemetry points made available to ERCOT must achieve a calendar quarterly availability of 99% percent.  Availability will be measured based on end-to-end connectivity of the communications path and the passing of Real-Time data with VALID quality codes at the scheduled periodicity.

1

Where:

A =	average percent availability of all points received from a given QSE or TSP.

T =	total number of seconds in the quarter.

i =	the ith point having a quality code other than VALID

n =	total number of points having a quality code other than VALID

Bi =	number of seconds during the quarter that the ith point had quality other than VALID.

Exceptions to Telemetry Availability calculation inputs:

- ERCOT declared Emergency Notice that can effect telemetry

- Total failure of the ERCOT WAN communication  system

- Restoration of Failed Telemetry and repair of inaccurate telemetry

Telemetered data shall be provided continuously at the scan rates specified herein.  Lost data or signals, whether failed or in error, must be restored promptly by the provider of the telemetered data.  It is recognized that some data may be more critical than other data.  ERCOT will inform the TSP or QSE if a data item is critical and needs to be repaired as quickly as possible.  QSE and TSP repair procedures and records shall be made available to ERCOT upon request.

Before ERCOT requests review/re-calibration of a problem piece of equipment it shall discuss the problem with the provider to attempt to arrive at a consensus decision on the most appropriate action.

When ERCOT notifies a data provider of a data element which is providing telemetry data inconsistent with surrounding measurements, the provider shall, within 30 days, either

- Calibrate/repair the malfunctioning equipment

- Request an outage to schedule calibration/repair of the malfunctioning equipment

- Provide ERCOT with a plan to re-calibrate or repair the equipment in a reasonable time frame or

- Provide ERCOT with engineering analysis proving the data element is providing accuracy within its specifications.

- Calibration, Quality Checking and Testing

It is the responsibility of the owner to insure that calibration, testing and other routine maintenance of equipment is done on a timely basis consistent with Good Utility Practice, for both the overall system and for individual equipment.

Coordination of outages required for these activities with ERCOT is also the responsibility of the owner.  If a TSP/QSE repeatedly fails other telemetry metrics defined in these Telemetry Criteria, ERCOT may require access to the preventative maintenance and calibration procedures and records.

- Reliability of ICCP links  [NP:3.10.7.5(4)]

Each TSP and QSE shall use fully redundant data communication links (between its control center systems and ERCOT systems such that any single element of the communication system can fail and:

- For server failures, complete information must be re-established within five minutes by automatic failover to alternate server(s); and

- For all other failures, complete information must continue to flow between the TSP’s, QSE’s, and ERCOT with updates of all data continuing at a 30 second or less scan rate.

ICCP links must achieve a rolling 12 month availability of _(99.8%) , excluding ERC OT approved planned outages of both redundant links.  Availability will be measured based on end-to-end connectivity of the either communications path continuing to provide of Real-Time data telemetry.  ERCPT shall establish a process to coordinate downtime for ICCP links and database maintenance such as to maintain continuity of data exchange between Market Participants and ERCOT.

## ERCOT Requests for Telemetry

Requests for Additional Telemetry [3.10.7.5 (5), (6), (7)]

ERCOT will request additional telemetry from QSEs and TSPs according to Nodal Protocol  including Section 3.10.7.5 (5), (6) and (7).

[ included here is the referenced protocols for discussion.

(5)  	When ERCOT identifies a reliability concern, a deficiency in system observability, or a deficiency in measurement to support the representation of Model Loads, and that concern or deficiency is not due to any inadequacy of the State Estimator program, ERCOT may request that a TSP or QSE provide additional telemetry measurements, beyond those required by the Telemetry Criteria, in a reasonable time frame for providing such measurements.  Such requests must be submitted to the TSP or QSE with a written justification for the additional telemetry measurements.  Such written justification must include documentation of the deficiency in system observability or representation of Model Loads.  In making the determination to request additional telemetry measurements, ERCOT shall consider the economic implications of inaccurate representation of Load Models in LMP results versus the cost to remedy.

(6)	Within 30 days of submittal by ERCOT to the designated contact of a TSP or QSE with a written request justifying additional telemetry measurements, the TSP or QSE shall acknowledge the request and either:

(a)	Agree with the request and make reasonable effort to install new equipment providing measurements to ERCOT within the timeframe specified;

(b)	provide ERCOT an analysis of the cost to comply with the request, so that, ERCOT can perform a cost justification with respect to the LMP market; or

(c)	if the TSP or QSE  disagrees with the request, appeal that request to TAC or present an alternate solution to ERCOT for consideration.

(7)	If ERCOT rejects the alternate solution, the TSP or QSE may appeal the original request to TAC within 30 days.  If, after receiving an appeal, TAC does not resolve the appeal within 65 days, the TSP or QSE may present its appeal to the ERCOT Board.  Notwithstanding the foregoing, a TSP or QSE is not required to provide telemetry measurements from a location not owned by that TSP or QSE, if the location owner does not grant access to the TSP or QSE for the purpose of obtaining such measurements.  ERCOT shall report such cases to the Wholesale Electric Market Monitor. end protocol quote]

# Compliance

# Compliance to the requirements o these Telemetry Criteria shall be governed by the PUCT-approved ERCOT compliance Process.

# Footnotes

The requirements for TSP and QSE telemetry have been separated into their own sections. Data exchange requirement are now in the ICCP Handbook rather than being listed in the Telemetry Standards.

Scan rate requirements have been changed to reflect the actual data exchange requirements of the market.

The Data Quality provision of the previous version of the Telemetry Standards addressed quality codes directly. Data quality is extensively treated in the ICCP Handbook, so this version of the Telemetry Standards refers to the ICCP Handbook.

Availability requires have been changed from 98% of all points achieving 80% availability, to all points achieving 99% availability. The 99% availability is the total availability of all points, not the availability of each point.

This requirement the number of voltage points to approximately 20... The previous version of the standard limited the number of voltage point to no more than 20.

A critical measurement is a measurement which will leave a portion of the transmission network un-observable if unavailable.

Availability of critical points has been changed from 95% of points having 98% availability to all points having 99.9% availability. The 99.9% availability is the total availability of all critical points, not the availability of each point

ICCP link availability has been changed to 99.9% from 85% to be consistent with the availability requirement for critical data.

# Comments

Footnotes in these Telemetry Criteria are temporary. They summarize the changes in this version from the previously TAC-approved version.

add TAC to verbiage

Request naming of document to specify "criteria" to match protocols

Change made 09/18/07

Continue to site number in protocol

This comment as written is not achievable due to latency issues.

The workshop group did not have a suggestion on the wording but acknowledge there is an issue with too much delay caused by daisy chaining the data from the field.

The intent is the maximum delay from source to ERCOT should be established.

What is quality code? Should be referred to in guides not handbook. description of process used in quality codes would be helpful. Potentially could include the code translations from the ICCP handbook.

QSE does not have ability to do algebraic sum. Remove QSE reference. Private networks cannot obtain this info. Paragraph is paraphrased from protocol, which changed intent of verbiage. Change to verbatim language from protocol  and for applicable area monitored. R6 should be done by ERCOT (where possible). Accountability discussion needed.

Modify to Substation instead of Electrical

Insert agreed upon perentage

Is this ERCOT measured in ERCOT's system?  If so, how do you account for issues w/in the ERCOT sys. Who is responsible for lost communication?  ERCOT does not have enough info to determine if this assessment is fair. Recommendation to use existing verbiage rather than edits.  Needs to include act-of-god, outage repair, etc.  Need definition formalized for "valid" quality codes. 99% listed not accepted by group. Scheduled outages not referenced in verbiage. need calculations, penalties, etc to set up shadow systems.

This is not formula for average availability.  Would like to change from the 100% requirement in the formula.  add factor of "n" to the "T" under the fornula - NxT= average availability. see above proposed change to equation.

Requested reword "ERCOT shall not" to something like "ERCOT will make every effort to contact the QSE", or add an exception statement for emergency situations.

Possibly "provide action-plan" as substitute for "fix".  Action plan would require inclusion of resolution.

Changed from "as soon as possible" to "within 1 day". Issues may not be able to be resolved within 1 day.  subsequent "action plan" statement would cover this situation - submitting a plan to cover the situation - possibly refer

Changed from "as soon as possible" to "within 1 day". Issues may not be able to be resolved within 1 day.  subsequent "action plan" statement would cover this situation - submitting a plan to cover the situation - possibly refer

Possibly add criteria on how to define critical points. Also criteria for determining an alternative means to resolve.

As defined in protocol 3.10.7.5.2 (1).  Possibly remove the word "Critical", or specify "criticality" definition

Need justification for percentage

what is observability?  What points impacted?  How long will ERCOT give to resolve?

singular/plural

Leave these comments in and add bullet referring to protocol.

determined to be unreasonable.  TSPs prefer prior verbiage

Is this ERCOT measured in ERCOT's system?  If so, how do you account for issues w/in the ERCOT sys. Who is responsible for lost communication?  ERCOT does not have enough info to determine if this assessment is fair. Recommendation to use existing verbiage rather than edits.  Needs to include act-of-god, outage repair, etc.  Need definition formalized for "valid" quality codes. 99% listed not accepted by group. Scheduled outages not referenced in verbiage. need calculations, penalties, etc to set up shadow systems.

Additional discussion of this topic is needed. Issue discussed but no final determination or agreement.

determined to be unreasonable.  TSPs prefer prior verbiage insert agreed upon percentage

strike - duplicate below

data provider referenced in other locations.  be consistent ("owner" preferred)

strike - owner covers this statement

request to remove this verbiage (j. varnell) or provide basis for this statement/requirement

change to "an owner"

insert rolling 12 month period statement needed.  Insert agreed upon percentage

Please remove "approved".

Please remove "approved".

Need to define "planned outages". How will these be tracked?

Insert agreed upon time frame

Insert agreed upon time frame

Significant changes - needs full review. what is data needed for, who is using it? 3/6 month time limits are not reasonable as a solid requirement rather than guideline.

Insert agreed upon time frame.

Insert agreed upon time frame